## Priced Summary
PHASE -II WORKS
NAME OF WORK : PROPOSED CONSTRUCTION OF ANCILLARY BUILDINGS, CIVIL WORKS AT TOOPRAN, MEDAK DIST.
CIVIL,SANITARY & WATER SUPPLY AND STRUCTURAL STEEL WORKS
S.NO | DESCRIPTION | AMOUNT (Rs.)
I | SUB HEAD -I SITE CLEARANCE | 260405
II | SUB HEAD -II EARTHWORK & EXCAVATION | 1381758.2
III | SUB HEAD III - ANTI-TERMITE TREATMENT | 132710
IV | SUB HEAD -IV PLAIN & REINFORCED CEMENT CONCRETE WORKS | 12000146.8969
V | SUB HEAD V - MASONARY WORK | 4010120
VI | SUB HEAD VI - PLASTERING & SURFACE TREATMENT | 3383475.5956
VII | SUBHEAD-VII : FALSE CEILING : | 71820
VIII | SUB HEAD -VIII FLOORINGS | 2315978
IX | SUB HEAD - IX JOINERY WORKS | 1091144
X | SUB HEAD -X ALUMINIUM WORKS | 91450
XI | SUB HEAD -XI WATER PROOFING | 1312360
XII | SUBHEAD- XII: STRUCTURAL STEEL WORK : | 6354698.5
XIII | SUB HEAD -XIII APPROACH ROADS | 745242
XIV | SUB HEAD -XIV SANITARY WORKS | 1217190
XV | SUB HEAD -XV EXTERNAL SEWAGE SYSTEM | 1883180
XVI | SUB HEAD -XVI WATER SUPPLY SERVICES | 1451300
| TOTAL AMOUNT Rs. | 37702978
| TOTAL AMOUNT | 37702978
| GST @ 18% | 6786536
| Grand Total Amount With Includig GST 18% | 44489514
Say Rs. 4.45 Cr

## Building Wise Priced Summary
PHASE -II WORKS
NAME OF WORK : PROPOSED CONSTRUCTION OF ANCILLARY BUILDINGS, CIVIL WORKS AT TOOPRAN, MEDAK DIST.
CIVIL,SANITARY & WATER SUPPLY AND STRUCTURAL STEEL WORKS
COST SUMMARY ( Trade Syndicate Final Rate Quote Item Wise)
S.No. | ITEM DESCRIPTION | AMOUNT | Buiding Wise Area IN sqm | Buiding Wise Area IN SFT | Buiding Wise Per SFT IN RS/-
1 | Contractor Toilet and Rest Room | 3110952 | 72 | 775 | 4014
2 | Workers Rest Room and Change Room | 5108292 | 148 | 1593 | 3207
3 | Health Care Center (G+1 Floor) | 6448798 | 236 | 2540 | 2539
4 | Security Extension | 870100 | 16 | 172 | 5059
5 | Scrap Yard Bins | 3776597.6 | 176 | 1894 | 1994
6 | Oil Store ( First Floor) | 1798314 | 114 | 1227 | 1466
7 | Parking Area Shed | 4957779.5 | 905 | 9741 | 509
8 | Search Barrier | 360225 | 36 | 387 | 931
9 | Ambulance Shed | 335945 | 12 | 129 | 2604
10 | Proposed Sump & Collection Sump | 417203 | 9 | 97 | 4301
11 | SMD (Office -1 ) Toilets | 529946 | 15 | 161 | 3292
12 | Approach Roads | 2755089 | 462 | 4973 | 554
13 | Septic Tank (100 Capacity) | 774017 | 49 | 527 | 1469
14 | External Services | 1908050 | 650 | 6996 | 273
15 | Plumbing works | 4551670
| BUILDING WORKS TOTAL AMOUNT IN RS. | 37702978.1
| TOTAL AMOUNT | 37702978.1
| GST @ 18% | 6786536
| GRAND TOTAL AMOUNT | 44489514.1
Say Rs. 4.45 Cr
MURTY & MANYAM
Architects & Engineers

## BUILDING WISE BOQ
Phase -II Works
PROPOSED CONSTRUCTION OF ANCILLARY BUILDINGS, OFFICES AND OTHER CIVIL WORKS AT VST PLANT , TOOPRAN, MEDAK DIST.
CIVIL,SANITARY & WATER SUPPLY AND STRUCTURAL STEEL WORKS
BILL OF QUANTITIES ( Revised After Centeral Excise Office Delete, Administration Building Delete, Existing Break Out Zone Delete , Oil Store Building Stair Case Deducted , All Sheds Building Rate Only Added Fixing (Labour) & Search Barrier Below Substructure Foundation Deducted)
S.NO | DESCRIPTION OF ITEMS | UNIT | RATE | 1. CONTRACTORS TOILET & REST ROOM |  | 2. WORKERS REST ROOM AND CHANGE ROOM |  | 3.HEALTH CARE CENTER (G+1 FLOOR) |  | 4.SECURITY EXTENSION |  | 5. SCRAP YARD BINS |  | 6. OIL STOR (FIRST FLOOR) |  | 7. PROPOSED PARKING SHED |  | 8. SEARCH BARRIER |  | 9.AMBULANCE SHED |  | 10.PROPOSED SUMP & COLLECTION SUMP |  | 11. FOR SMD (OFFICE-1) TOILET |  | 12. APPROACH ROADS |  | 13. Septic Tank 100 Capcity |  | 14. EXTERNAL SERVICES |  | QUANTITY | AMOUNT
|  |  |  | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT | QTY | AMOUNT
SUB HEAD -I SITE CLEARANCE
1 | Clearing jungle including uprooting of rank vegetation, grass, brush wood, trees and saplings of girth up to 30 cm measured at a height of 1 m above ground level and removal of rubbish up to a distance of 50 m outside the periphery of the area cleared | Sqm | 18 | 211 | 3798 | 326 | 5868 | 258 | 4644 | 0 | 0 | 385 | 6930 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 1980 | 111 | 1998 | 0 | 0 | 509 | 9162 | 200 | 3600 | 650 | 11700 | 2760 | 49680
2 | Felling trees of the girth (measured at a height of 1 m above ground level), including cutting of trunks and branches, removing the roots and stacking of serviceable material and disposal of unserviceable material. (With in Building Area trees only to be consider.)
| Beyond 30 cm girth upto and including 60 cm girth | Each | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 960 |  |  | 2 | 960 | 4 | 1920
| Beyond 60 cm girth upto and including 120 cm girth | Each | 1995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1995 |  |  | 1 | 1995 | 2 | 3990
| Beyond 120 cm girth upto and including 240 cm girth | Each | 10395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10395 |  |  | 1 | 10395 | 2 | 20790
3 | Hacking and chipping existing surfaces including cleaning for surface etc. complete as per direction of the Engineer-in-Charge | Sqm | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4030 | 115 | 35650 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 128 | 39680
4 | Dismantling CRS stone MASONRY, marble work or precast concrete work manually/ by mechanical means including stacking of serviceable and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge : | Cum | 2635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 65875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2635 | 0 | 0 |  |  | 0 | 0 | 26 | 68510
5 | Demolishing R.C.C columns,walls and beams work, VDF Flooring manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of Engineer - in- charge. | Cum | 2910 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14550 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2910 | 0 | 0 |  |  | 0 | 0 | 6 | 17460
6 | Demolishing cement concrete , solling and PCC stone manually/ by mechanical means including disposal of material within 50 metres lead as per direction of Engineer - in - charge | Cum | 1385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1385 | 0 | 0 |  |  | 0 | 0 | 1 | 1385
7 | Drilling suitable holes in reinforced or plain cement concrete with power driven drill machine to a minimum depth of 100 mm upto 200 mm in RCC beams, lintels, columns and slabs to introduce steel bars for sunshades/ balconies including fixing the steel bars in position using epoxy resin anchor grout of approved make but excluding the cost of reinforcement, all complete as per direction of Engineer-In-Charge ( Up to12mm dia to 30mm diameter to the existing stone masonry/RCC structure) | Each | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 12500 | 50 | 6250 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 1250 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 160 | 20000
8 | Dismantling tile work in floors with chipping and removing ceramic tiles including plastering on walls and floors laid in cement mortar including stacking material within 50 metres lead. For thickness of tiles 10 mm to 25 mm | Sqm | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
9 | Dismantling doors, windows,Vintilator and clerestory windows (steel , Aluminium or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead : For Existing Buildings
| Of area 3 sq. metres and below | Each | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 10 | 3600
10 | Dismantling wood work in frames, trusses, purlins and rafters up to 10 metres span and 5 metres height including stacking the material within 50 metres lead :
| Of sectional area 40 square centimetres and above | Cum | 3800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
11 | Dismantling roofing including ridges, hips, valleys and gutters etc., and stacking the material as per direction of Engineer-in-charge. Dismalting of G.S Sheet | Sqm | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
12 | Dismantling G.I. pipes (internal and external work) including excavation and refilling trenches after taking out the pipes, manually/ by mechanical means including stacking of pipes within 50 metres lead as per direction of Engineer-in-charge( 15 mm to 40 mm nominal bore) Existing old pipes after chipping wall are moving. | Rmt | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
13 | Dismantling of flushing cistern of all types (C.I./PVC/Vitrious China) including stacking of useful materials near the site and disposal of unserviceable materials within 50 metres lead. | Each | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
14 | Demolishing brick work manually/by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge.
| In cement mortar | Cum | 1890 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 10 | 18900
15 | Demolishing stone rubble masonry manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge : | Cum | 2247 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 5 | 11235
16 | Removing mortar from and cleaning stones and concrete articles (net quantity of stacks of cleaned materials will be measured): | cum | 651 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 5 | 3255
| SUB HEAD - I TOTAL AMOUNT |  |  |  | 3798 |  | 5868 |  | 4644 |  | 49170 |  | 133605 |  | 0 |  | 0 |  | 0 |  | 3230 |  | 1998 |  | 6930 |  | 22512 |  | 3600 |  | 25050
SUB HEAD -II EARTHWORK & EXCAVATION
17 | Earth work in excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5 m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including getting out the excavated soil and disposal of surplus excavated soil as directed, within a lead of 50 m. as per approved drawings/as directed by Engineering-in-Charge.
All kinds of soil.
| a) All kinds of soil Lift upto 1.50M | Cum | 240 | 85 | 20400 | 138 | 33120 | 123 | 29520 | 16 | 3840 | 53 | 12720 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 3360 | 23 | 5520 | 0 | 0 | 496 | 119040 | 54 | 12960 | 750 | 180000 | 1752 | 420480
| b) All kinds of soil 1.50M to 3.00M | Cum | 320 | 64 | 20480 | 109 | 34880 | 101 | 32320 | 11 | 3520 | 37 | 11840 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 2240 | 4 | 1280 | 0 | 0 | 0 | 0 | 36 | 11520 | 0 | 0 | 369 | 118080
| c) All kinds of soil 3.00M to 4.50M | Cum | 440 | 43 | 18920 | 73 | 32120 | 101 | 44440 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 6160 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 231 | 101640
| c) All kinds of soil 4.50M to 6.00M | Cum | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 4860 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 9 | 4860
18 | Close timbering in case of shafts, wells, cesspits, manholes and the like including strutting, shoring and packing cavities (wherever required) etc. complete. (Measurements to be taken of the face area timbered).
| a) Depth not exceeding 1.5 m | Sqm | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 300 | 0 | 0 | 50 | 7500 |  |  | 75 | 11250 | 127 | 19050
| b) Depth exceeding 1.5 m but not exceeding 3 m | Sqm | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 169 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1 | 169
| c) Depth exceeding 3 m but not exceeding 4.5 m | Sqm | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 768 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 4 | 768
| d) Depth exceeding 4.5m but not exceeding 6.00 m | Sqm | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 900 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 4 | 900
19 | Carting away exacvated excess soil,debris and dispose the same within the premises as direceted by engineer incharge | Cum | 268 | 20 | 5360 | 20 | 5360 | 20 | 5360 | 7 | 1876 | 30 | 8040 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 3752 | 27 | 7236 | 0 | 0 | 400 | 107200 |  |  | 0 | 0 | 538 | 144184
20 | Carting away of outside premises of excavated earth, building debris etc., including cost and conveyance of all conveyance, labour, tools and tackles complete for finished item of work. | Cum | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2 | 8748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 14580 | 3 | 1620 | 400 | 216000 |  |  | 0 | 0 | 446.2 | 240948
21 | Re-filling with useful available excavated earth other than expansive soils like red earth and ordinary gravel etc., (excluding rock) in trenches, sides of foundations and basement with initial lead in layers not exceeding 15 cm thick, consolidating each deposited layer by watering and ramming including cost and conveyance of breaking clods, storing, transportation, double handling, watering, compacting each layer with vibratory compactor and at unaccessible places with wooden/ steel rammers to achieve 98% proctor density at optimum moisture content, of water to work site and all incidental, operational, labour charges , hire charges of t & p etc., complete for finished item of work. . | Cum | 179 | 192 | 34368 | 320 | 57280 | 325 | 58175 | 10.8 | 1933.2 | 90 | 16110 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 3759 | 0 | 0 | 0 | 0 | 96 | 17184 |  |  | 0 | 0 | 1054.8 | 188809.2
22 | Supply and filling in foundations and the area where ever specified with approved good quality filling materials in plinths, area development etc., where ever specified in layers of not exceeding 150 mm thick including breaking clods, storing, transportation, double handling, watering, compacting each layer with vibratory compactor with road roller 8 to 12 tonnes capacity and at unaccessible places with wooden/ steel rammers to achieve 98% proctor density at optimum moisture content, all leads and lifts, bailing/ pumping out of water to keep site dry while backfilling; cost shall include conveyance of all materials, labour, machinery etc., complete as directed. The rate to includes loading, unloading, hire and fuel charges for tools and plants and other incidental charges etc., complete as directed by Consultant.With approved quality filling Morroum brought from outside | Cum | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 10470 | 0 | 0 | 152 | 106096 |  |  | 0 | 0 | 175 | 122150
23 | Supplying and filling in Plinth With sand at site including royalty and carriage in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering complete, as per approved drawings/as directed by Engineering-in-Charge. Filling Sand | Cum | 1972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19720 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 10 | 19720
| SUB HEAD - II TOTAL AMOUNT |  |  |  | 99528 |  | 162760 |  | 169815 |  | 19917.2 |  | 54294 |  | 0 |  | 0 |  | 0 |  | 13111 |  | 71963 |  | 1620 |  | 573020 |  | 24480 |  | 191250
SUB HEAD III - ANTI-TERMITE TREATMENT
24 | Providing pre constructional anti termtite treatment by injecting Imidacloprid 30.5% SC with 0.075% concentration complete and creating a continuous barrier under and alround the column pits, wall trenches, basement excavation, top surface of plinth filling, junction of wall and floor, along the external perimeter of building, expansion joints, over the top surface of consolidated earth on which apron is to be laid, surroundings of pipes and conduits etc., complete as per specification and stipulations laid down in IS 6313 (Part II). (Plinth area of the building at ground floor level only shall be measured for payment). (To be executed by specialist agency, pest control (India) Ltd. or equivalent approved agency. Guarantee period for 10 years). complete as directed by Engineer-In-Charge.
| Imidacloprid 30.5% SC with 0.075% concentration or equivalent as per manufacturer specifications. | Sqm | 230 | 72 | 16560 | 146 | 33580 | 122 | 28060 | 15 | 3450 | 190 | 43700 | 0 | 0 | 0 | 0 |  | 0 | 12 | 2760 | 20 | 4600 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 577 | 132710
| SUB HEAD - III TOTAL AMOUNT |  |  |  | 16560 |  | 33580 |  | 28060 |  | 3450 |  | 43700 |  | 0 |  | 0 |  | 0 |  | 2760 |  | 4600 |  | 0 |  | 0 |  |  |  | 0
SUB HEAD -IV PLAIN & REINFORCED CEMENT CONCRETE WORKS
25 | Providing and laying plain cement concrete 1:4:8(1: cement 4: coarse sand 8: graded stone aggregate 40mm nominal size ) using H. B. G(Hard borken granite) coarse graded aggregate of 40 mm and down size for levelling course under footings, steps, walls, platform& ramps etc., including laying layers of specified thickness in alternative bays not exceeding 10 sqm as directed including form work wherever necessary and well compacted etc., all complete, as directed by Engineer-in-charge/Architect.(Grade of Mix 7.5) | Cum | 5125 | 14 | 71750 | 27 | 138375 | 24 | 123000 | 3 | 15375 | 23 | 117875 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 15375 | 2 | 10250 | 2.4082 | 12341.8969 | 51 | 261375 | 4 | 20500 | 150 | 768750 | 303.4082 | 1554966.8969
26 | Providing and laying 50mm average thick PCC 1:3:6 (1 Cement : 3 Coarse sand and 6 Graded stone aggregate 20mm nominal size) for Plinth Protection over 75mm thick dry cement concrete aggregate of 40mm nominal size well rammed, consolidated and grouted with fine sand inlcuding finishing the top smooth with extra cement mortar of (1:3) prop with a floating coat of neat cement finish and filling the construction joints with sand,bitumen at every 15m .The exposed edges are to be protected with CC brick edging by placing the bricks vertically completed all as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 550 | 32 | 17600 | 43 | 23650 | 36 | 19800 | 0 | 0 | 32 | 17600 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3850 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 150 | 82500
READY MIX CONCRETE / CONTROLLED CONCRETE
27 | providing and laying in position ready mixed or site batched design mix cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived fromnatural sources, portland pozzolana / ordinary portland /portland Slag cement, admixtures in recommended proportions as per iS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering,finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. as per approved drawings/as directed by Engineering-in-Charge. Note: in case the cement content in design mix is more than thespecified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. Concrete of M25 Grade with Minimum Cement Content of 330 kg/Cum
| a) All Works upto Plinth Level | Cum | 8150 | 23 | 187450 | 38 | 309700 | 38 | 309700 | 4 | 32600 | 37 | 301550 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 32600 | 10 | 81500 | 0 | 0 | 0 | 0 | 18 | 146700 | 0 | 0 | 172 | 1401800
| b) All Works above plinth and upto 8.50m Height | Cum | 8460 | 20 | 169200 | 41 | 346860 | 61 | 516060 | 5 | 42300 | 0 | 0 | 20 | 169200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 147 | 1243620
28 | Reinforced cement concrete work in lintels (any thickness), including attached pilasters,buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts andstruts etc. above pinth level up to V floor level, excluding cost of centering, shuttering,finishing and reinforcement : 1:1.5:3 (1 cement : 1.5 coarse sand(zone-iii) derived from natural sources : 3 graded stoneaggregate 20 mm nominal size derived from natural sources as per approved drawings/as directed by Engineering-in-Charge. | Cum | 7700 | 4 | 30800 | 5 | 38500 | 7 | 53900 | 1 | 7700 | 0 | 0 | 3 | 23100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 20 | 154000
29 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral staircases above plinth level up to fifth floor level excluding the cost of centering, shuttering, finishing and reinforcement, with 1:1.5:3 (1 cement : 1.5 coarse sand incuding anufactured sand derived from recycled concrete Aggregate (rcA) upto 20%: 3 graded stone aggregate 20 mm nominal size including recycled concrete Aggregate (rcA) upto 20%) as per approved drawings/as directed by Engineering-in-Charge. | Cum | 8200 | 2 | 16400 | 3 | 24600 | 2 | 16400 | 1 | 8200 | 0 | 0 | 2 | 16400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 10 | 82000
30 | Providing and laying in position specified grade of reinforced cement concrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work upto plinth level 1:2:4 (1 cement : 2 coarse sand (zone-iii) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources ) complete for finished item of work as directed by Engineer in charge as per approved drawings/as directed by Engineering-in-Charge. | Cum | 6450 | 2 | 12900 | 2 | 12900 | 2 | 12900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 12900 | 0 | 0 |  |  | 0 | 0 | 8 | 51600
31 | Providing & laying reinforced cement concrete in 1:2:4 mix by volume including cost of cement, steel, all materials ,labour and form work centering, shuttering , scaffolding,curing etc item includes smooth finishing with cement mortar ( 1:3) on the exposed surface complete finishing item of work at all floors including fixing of slab as per drawing as directed by Engineer-in-charge.(consider reinforcement steel as 6Kg/Sqm.) 50mm Thick RCC Counter Slab | Sqm | 410 | 5 | 2050 | 5 | 2050 | 5 | 2050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2050 | 0 | 0 |  |  | 0 | 0 | 20 | 8200
32 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete. as per approved drawings/as directed by Engineering-in-Charge.
| Thermo-Mechanically Treated bars | Kgs | 98 | 6647 | 651406 | 12180 | 1193640 | 15488 | 1517824 | 1470 | 144060 | 5985 | 586530 | 3486 | 341628 | 0 | 0 | 0 | 0 | 546 | 53508 | 1407 | 137886 | 0 | 0 | 3305 | 323890 | 3909 | 383082 | 0 | 0 | 54423 | 5333454
33 | Providing, fabricating and erecting of steel form work at all levels and places wherever needed/ specified as per drawing including striking with not less than 12mm Plastic coated, marine resistant water proof ply/ smooth finished MS plates with adjustable steel props of acceptable staging system and with sufficient bracing as approved by consultant. Cost to include designing of proper form work and staging system to suit the requirements, Submission of design calculations and shop drawings for approval, sealing the joints with heavy duty brown self adhesive tape, aligning to line and levels including M.S. Ties (including grouting), PVC Spacer/Precast cover blocks, Providing openings/ cutouts/ pockets, deshuttering, applying chemical for shuttering as approved by the consultant etc., complete at all levels, as per approved drawings/as directed by Engineering-in-Charge.
| a) Foundations, footings, bases of columns, etc. for mass concrete | Sqm | 345 | 30 | 10350 | 53 | 18285 | 50 | 17250 | 6 | 2070 | 50 | 17250 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1725 | 4 | 1380 | 0 | 0 | 56 | 19320 | 5 | 1725 | 0 | 0 | 259 | 89355
| b) Columns, Pillars, Piers, Abutments, Posts and Struts | Sqm | 815 | 85 | 69275 | 185 | 150775 | 225 | 183375 | 18 | 14670 | 69 | 56235 | 38 | 30970 | 0 | 0 | 0 | 0 | 6 | 4890 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 626 | 510190
| c) Suspended floors, roofs, landings, chajja's , balconies and access platform | Sqm | 775 | 115 | 89125 | 173 | 134075 | 257 | 199175 | 25 | 19375 | 18 | 13950 | 129 | 99975 | 0 | 0 | 0 | 0 | 10 | 7750 | 10 | 7750 | 0 | 0 | 0 | 0 | 24 | 18600 | 0 | 0 | 761 | 589775
| d) Lintels, beams, plinth beams, girders, bressumers and cantilevers | Sqm | 570 | 155 | 88350 | 264 | 150480 | 307 | 174990 | 36 | 20520 | 63 | 35910 | 103 | 58710 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 928 | 528960
| e) staircases | Sqm | 620 | 0 | 0 | 32 | 19840 | 32 | 19840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 64 | 39680
| f) Walls (any thickness) including attached pilasters, butteresses, plinth and string courses etc. | Sqm | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 38076 | 0 | 0 | 0 | 0 | 100 | 66800 | 0 | 0 | 157 | 104876
34 | Laying, spreading and compacting stone aggregate of specified sizes to Rubble soling (230mm thick) specifications in uniform thickness, hand picking, rolling with 3 wheeled road/vibratory roller 8-10 tonne capacity in stages to proper grade and camber, applying and brooming requisite type of screening / binding material to fill up interstices of coarse aggregate, watering and compacting to the required density . as per approved drawings/as directed by Engineering-in-Charge. | Cum | 890 | 18 | 16020 | 37 | 32930 | 31 | 27590 | 3 | 2670 | 44 | 39160 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 2670 | 0 | 0 | 0 | 0 | 117 | 104130 |  |  | 0 | 0 | 253 | 225170
| SUB HEAD - IV TOTAL AMOUNT |  |  |  | 1432676 |  | 2596660 |  | 3193854 |  | 309540 |  | 1186060 |  | 739983 |  | 0 |  | 0 |  | 122368 |  | 276842 |  | 27291.8969 |  | 708715 |  | 637407 |  | 768750
SUB HEAD V - MASONARY WORK
35 | Random rubble masonry with hard stone in foundation and plinth including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with :Cement mortar 1:6 (1 cement : 6 coarse sand ,as per approved drawings/as directed by Engineering-in-Charge. | Cum | 6770 | 18 | 121860 | 28 | 189560 | 30 | 203100 | 4 | 27080 | 4 | 27080 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 54160 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 92 | 622840
36 | Providing and laying Concrete Block masonry in super structure above plinth level up to V level. blocks conforming to IS 2185 part (2) as per manufacture specification laid in cement mortar 1:6 (1 cement :6 coarse M-Sand),for non-load bearing walls and a suitable plasticizer. Masonry work shall be carried out as per IS 2185 part (2). The rate shall include cost of cement and all materials etc. curing, scaffolding wherever necessary complete as per specification. Crushing strength 5N/mm2 .size 300x200x200mm as per approved drawings/as directed by Engineering-in-Charge. | Cum | 8840 | 25 | 221000 | 49 | 433160 | 44 | 388960 | 5 | 44200 | 89 | 786760 | 20 | 176800 | 0 | 0 | 0 | 0 | 2 | 17680 | 0 | 0 | 7 | 61880 | 0 | 0 |  |  | 100 | 884000 | 341 | 3014440
37 | Providing and laying Concrete Block masonry in super structure above plinth level up V level. blocks conforming to IS 2185 part (2) as per manufacture specification laid in cement mortar 1:4 (1 cement :4 coarse M-Sand),for non-load bearing walls and a suitable plasticizer. Masonry work shall be carried out as per IS 2185 part (2). The rate shall include cost of cement and all materials etc. curing, scaffolding wherever necessary complete as per specification. Crushing strength 40N/mm2 .size 300x150x100mm including RCC band complete for providing and placing in position 2 Nos 6mm dia. M.S. bars at every third course of half brickmasonry. Brick Size : 100mm Thick Brick Wall finished item of work. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 780 | 69 | 53820 | 49 | 38220 | 161 | 125580 | 4 | 3120 | 41 | 31980 | 73 | 56940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 24180 | 0 | 0 |  |  | 50 | 39000 | 478 | 372840
38 | Brick work with common burnt clay loal available bricks of compressive strength 35N/Sq.mm. in superstructure above plinth level up to floor V level in all shapes and sizes in :1:6 (1 cement : 6 coarse sand) : With Modular bricks Size : 230mm Thick Brick Wall as per approved drawings/as directed by Engineering-in-Charge. | Cum | 8340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
39 | Half brick masonry with common burnt clay local available bricks of compressive strength 35N/Sq.mmin. superstructure above plinth level up to floor V level. Cement mortar 1:4 (1 cement :4 coarse sand) wit providing and placing in position 2 Nos 6mm dia. M.S. bars at every third course of half brick masonry. Brick Size : 115mm Thick Brick Wall as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 1039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| SUB HEAD - V TOTAL AMOUNT |  |  |  | 396680 |  | 660940 |  | 717640 |  | 74400 |  | 845820 |  | 233740 |  | 0 |  | 0 |  | 71840 |  | 0 |  | 86060 |  | 0 |  |  |  | 923000
SUB HEAD VI - PLASTERING & SURFACE TREATMENT
40 | 6 mm cement plaster 1:3 (1 cement : 3 fine sand) finished with a floating coat of neat cement and thick coat of Lime wash on top of walls when dry for bearing of R.C.C. slabs and beams at all Levels. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 340 | 142 | 48280 | 257 | 87380 | 391 | 132940 | 27 | 9180 | 0 | 0 | 126 | 42840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 7140 | 0 | 0 | 964 | 327760
41 | Providing & laying 15 mm thick cement Plaster to Internal walls columns, piers etc. in cement mortar 1 : 4 (1 cement : 4 sand; 75% fine sand & 25% coarse sand) on plain side of wall or R.C.C. surface including fixing 150 mm Wide Plaster mesh made out of galvanized iron of nominal thickness 0.35 mm at the junctions of Masonry and concrete works, chasing Works 200 mm Width, Diagonal fixing at Doors & Windows Opening to a width of 300 mm x 600 mm; Corner Bead of size 45 x 45 mm made out of galvanized iron of nominal thickness 0.45 mm with a Zinc coating of 120 gms per Sqm as protector for plastered wall and column corners/edges from chipping, including tying in position by using suitable nails / clamps / screws including tying in position mesh jali between RCC and masonry wall and making grooves with suitable nails / screws etc., complete and as per manufacturer specification of approved make. Rate shall include for preparation of surface, cleaning, curing, scaffolding hacking, labour materials etc. complete for all levels and heights as directed. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 430 | 222 | 95460 | 355 | 152650 | 462 | 198660 | 38 | 16340 | 609 | 261870 | 231 | 99330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 46870 | 0 | 0 |  |  | 0 | 0 | 2026 | 871180
42 | Providing and Laying 18mm thick sand faced cement plastering on external surfaces of Walls (brick or concrete surfaces ) in two layers consisting of 6 mm thick cement mortar 1:3 (1 cement :3 fine sand) top coat mixed with integral water proofing compound over a base coat 12 mm thick cement mortar 1:5 (1 cement :5 coarse sand), finished sand face including providing and fixing 12mmx22mm gauge chicken mesh with all necessary hardware at the junction of RCC and brick work with overlapping of 100 mm on both sides, etc., complete at all levels and locations and as directed by Engineer - in - Charge. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 470 | 252 | 118440 | 339 | 159330 | 441 | 207270 | 47 | 22090 | 196 | 92120 | 214 | 100580 | 0 | 0 | 0 | 0 | 16 | 7520 | 0 | 0 | 51 | 23970 | 0 | 0 | 47 | 22090 | 0 | 0 | 1603 | 753410
43 | Providing average 20mm thick cement plaster in two coats, 1st coat 14mm thick in CM (1:6) and top coat 6mm thick in CM (1:4), mixed , finishing the surface smooth and even shade, making the corner true including curing scaffolding, hacking, grooves etc., complete over brick walls and RCC surfaces to the exterior face of the building, interernal and external faces of RCC Surface ,jambs complete including roughening first coat plaster surface to receive 2nd and final coat of plaster but including cost of cement.as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
44 | Pointing on stone work with cement mortar 1:3 (1 cement : 3 fine sand)Raised and cut pointing as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 595 | 0 | 0 | 0 | 0 | 43 | 25585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 43 | 25585
45 | Providing plaster drip course/water patti in plastered surface or moulding to R.C.C projections Slab Parapet Watter Patti & Windows including cost and conveyance of all materials labour charges, scaffolding complete for finished item of work as per approved drawings/as directed by Engineering-in-Charge. | Rmt | 157 | 86 | 13502 | 114 | 17898 | 95 | 14915 | 29 | 4553 | 0 | 0 | 85 | 13345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 409 | 64213
46 | Providing, mixing and applying bonding coat of approved adhesive on chipped portion of RCC as per specifications and direction of Engineer- In-charge complete in all respect. SBR Polymer (@10% of cement weight) modified cementitious bond coat @ 2.2 kg cement per sqm of surface area mixed with specified proportion of approved polymer as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 7500 | 30 | 4500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 80 | 12000
47 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer Colour, over the plastered wall surface to prepare the surface even and smooth complete for finished item of work as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 120 | 616 | 73920 | 951 | 114120 | 1294 | 155280 | 112 | 13440 | 0 | 0 | 445 | 53400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 19200 | 0 | 0 |  |  | 0 | 0 | 3578 | 429360
48 | Providing and applying priming coats with primer of approved brand and manufacture, having low VOC (Volatile Organic Compound ) content. With water thinnable cement primer on internal and external wall surface having VOC content less than 50 grams/litre including preparation of surface, scaffolding at all heights and levels etc., as per Directions of Engineer -In- Charge for the finished item of work. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 62 | 616 | 38192 | 951 | 58962 | 1294 | 80228 | 112 | 6944 | 805 | 49910 | 445 | 27590 | 0 | 0 | 0 | 0 | 16 | 992 | 0 | 0 | 160 | 9920 | 0 | 0 |  |  | 0 | 0 | 4399 | 272738
49 | Providing and applying Wall painting of approved brand and manufacture, with premium acrylic emulsion paint of interior grade, having VOC (Volatile Organic Compound ) content less than 50 grams/ litre of approved brand and manufacture, including applying additional coats wherever required to achieve even shade and colour. (Internal finishing side)Two coats colour and quality to give an even shade including preparation of surface, scaffolding at all heights and levels etc., as per Directions of Engineer -In- Charge for the finished item of work. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 128 | 364 | 46592 | 612 | 78336 | 853 | 109184 | 65 | 8320 | 609 | 77952 | 231 | 29568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 13952 | 0 | 0 |  |  | 0 | 0 | 2843 | 363904
50 | Providing and applying painting of approved brand and manufacture , with Acrylic Smooth exterior emulsion paint of required shade :New work (Two or more coat applied @ 1.67 ltr/10 sqm overand including priming coat of exterior primer applied @ 0.90 litre/10 sqm)colour and quality to give an even shade including preparation of surface, scaffolding at all heights and levels etc., as per Directions of Engineer -In- Charge for the finished item of work. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 142 | 252 | 35784 | 339 | 48138 | 441 | 62622 | 47 | 6674 | 196 | 27832 | 214 | 30388 | 0 | 0 | 0 | 0 | 16 | 2272 | 0 | 0 | 51 | 7242 | 0 | 0 |  |  | 0 | 0 | 1556 | 220952
51 | White washing with lime to give an even shade New work (three or more coats) :complete all as directed by Engineer - in - Charge. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 4032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 126 | 4032
52 | Providing and applying Painting on Steel and Wood Surface with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade :New work (two coats) including a coat of approved steel primer but excluding a coat of mordant solution, as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 154 | 11 | 1694 | 7 | 1078 | 24 | 3696 | 0 | 0 | 196.9714 | 30333.5956 | 3 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1078 | 0 | 0 |  |  | 0 | 0 | 248.9714 | 38341.5956
| SUB HEAD - VI TOTAL AMOUNT |  |  |  | 471864 |  | 717892 |  | 990380 |  | 95041 |  | 544517.5956 |  | 401535 |  | 0 |  | 0 |  | 10784 |  | 0 |  | 122232 |  | 0 |  | 29230 |  | 0
SUBHEAD-VII : FALSE CEILING :
53 | Providing and fixing mineral fibre false ceiling tiles at all heights of size 595X595mm of approved texture, design and pattern. The tiles should have Humidity Resistance (RH) of 99%, Light Reflectance ≥ 85%, Thermal Conductivity k = 0.052 - 0.057 w/m K, Fire Performance as per (BS 476 pt - 6 &7)in true horizont al level suspended on interlocking T-Grid of hot dipped all round galvanized iron section of 0.33 mm thick (galvanized @120 gsm) comprising of main T runners of 15x32 mm of length 3000 mm, cross T of size 15x32mm of length 1200 mm and secondary intermediate cross T of size 15x32 mm of length 600 mm to form grid module of size 600x600 mm suspended from ceiling using galvanized mild steel item (galvanised@80gsm) 50 mm long 8mm outer diameter M-6 dash fasteners, 6 mm diameter fully threaded hanger rod up to 1000 mm length and L-shape level adjuster of size 85x25x2 mm, spaced at 1200 mm centreto centre along main ‘T’. The system should rest on periphery walls /partitions with the help of GI perimeter wall angle of size24x24X3000 mm made of 0.40 mm thick sheet, to be fixed to the wall with help of plastic rawl plug at 450 mm centre to centre & 40 mm long dry wall S.S. screws. The exposed bottom portion of all T-sections used in false ceiling support system shall be pre-painted with polyester baked paint, for all heights. The work shall be carried out as per specifications, drawings and as per directions of the engineer-in-charge.26.27.1With 16 mm thick beveled tegular mineral fibre false ceiling tile (NRC 0.55 to 0.60) as per approved drawings/as directed by Engineering-in-Charge. For Toilets | Sqm | 1890 | 0 | 0 | 0 | 0 | 12 | 22680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 49140 | 0 | 0 |  |  | 0 | 0 | 38 | 71820
| SUB HEAD - VII TOTAL AMOUNT |  |  |  | 0 |  | 0 |  | 22680 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 49140 |  | 0 |  | 0 |  | 0
SUB HEAD -VIII FLOORINGS
54 | Providing and laying VDF. flooring and platforms , Roads of mix M-25 with ready mixed concrete from batching plant. The ready mixed concrete shall be laid and finished with screed board vibrator, vacuum dewatering process and finally finished by floating, brooming with wire brush etc. complete as per specifications and directions of Engineer-incharge. (The panel shuttering work shall be paid for separately). (Note:- Cement content considered in this item is @ 330 kg/Cum. Excess/ less cement used as per design mix is payable/ recoverable separately). | Cum | 8820 | 0 | 0 | 0 | 0 | 6 | 52920 | 0 | 0 | 23 | 202860 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 17640 | 0 | 0 | 0 | 0 | 80 | 705600 |  |  | 0 | 0 | 111 | 979020
55 | Cutting grooves 4mmx20mm deep in vaccum dewatered flooring with diamond saw cutting machine before the concrete is 7days old including providing & filling the grooves with poly sulphide of apporved make or equivalent ( modified semi - rigid epoxy joint filler). | Rmt | 41 | 0 | 0 | 0 | 0 | 7 | 287 | 0 | 0 | 27 | 1107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 34 | 1394
56 | 62 mm thick cement concrete flooring with concrete hardener topping, under layer 50mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) and top layer 12mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate, 6mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacture’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc. complete as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 27600 | 0 | 0 | 30 | 27600
57 | Providing and laying Double charge vitrified tile polished finish of size (thickness to be specified by the manufacturer) with water absorption less than 0.08% and conforming to IS:15622, of approved brand & manufacturer, in all colours and shade, laid on 20 mm thick cement mortar 1:4 (1 cement: 4 coarse sand) jointing with grey cement slurry @3.3 kg/sqm including grouting the joints with white cement and matching pigments etc. The tiles must be cut with the zero chipping diamond cutter only . Laying of tiles will be done with the notch trowel, plier, wedge, clips of required thickness, leveling system and rubber mallet for placing the tiles gently and easily.Double charge vitrified tile polished finish of size Size of Tile 600 x 600 mm as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 1898 | 47 | 89206 | 147 | 279006 | 84 | 159432 | 13 | 24674 | 0 | 0 | 78 | 148044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 369 | 700362
58 | Providing and laying premium quality double charged polished finished Vitrified Floor Tiles of size 600x600mm, 8.5mm thick for Skirting of with water absorptions less than 0.08% and confirming to IS:15622 of approved make in all colours and shades, laid on 20mm thick cement mortar 1:4 (1 cement:4 coarse sand) including grouting the joints with white cement and matching pigments, curing etc., complete at all levels and heights. as directed by Engineer-In-Charge.Inside Room as per approved drawings/as directed by Engineering-in-Charge | Sqm | 2098 | 3 | 6294 | 8 | 16784 | 11 | 23078 | 2 | 4196 | 0 | 0 | 4 | 8392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 28 | 58744
59 | Cement skirting 150mm high in CM (1:3) 18mm thick finished with a floating coat of neat cement etc., complete. | Sqm | 598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 8970 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 15 | 8970
60 | Kota stone slab flooring over 20 mm (average) thick base laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab, including rubbing, nosing and polishing complete with base of cement mortar 1 : 4 (1 cement : 4 coarse sand) : as per approved drawings/as directed by Engineering-in-Charge. 25 mm thick FOR STEPS | Sqm | 1670 | 7 | 11690 | 9 | 15030 | 40 | 66800 | 2 | 3340 | 21 | 35070 | 26 | 43420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 105 | 175350
61 | Supplying and fixing approved first quality Non skid ceramic tiles in toilets etc. of approved shade with tiles of size 300 x 300mm , 6mm thick jointed in neat cement and matching pigment over and including a screed of 20mm thick CM 1:4, including curing and washing with oxalic acid in flooring complete at all levels and heights as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 1010 | 21 | 21210 | 0 | 0 | 6 | 6060 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14140 | 0 | 0 |  |  | 0 | 0 | 41 | 41410
62 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of size (300 x600mm & 600x600mm) as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. as per approved drawings/as directed by Engineering-in-Charge.
| a) Size 300x600mm | Sqm | 1075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| b) Size 600x600mm | Sqm | 1352 | 133 | 179816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 143312 | 0 | 0 |  |  | 0 | 0 | 239 | 323128
| SUB HEAD - VIII TOTAL AMOUNT |  |  |  | 308216 |  | 310820 |  | 308577 |  | 32210 |  | 248007 |  | 199856 |  | 0 |  | 0 |  | 17640 |  | 0 |  | 157452 |  | 705600 |  | 27600 |  | 0
SUB HEAD - IX JOINERY WORKS
63 | Supplying and fixing of Single shutter door using door frames fabricated from sections made of galvanized steel powder coated (base steel as per IS 513, galvanized as per IS 277 with zinc of 120 grams / square metre), the factory made section are powder coated with pure polyester powder of 50-60 microns thick with total coated thickness of 1.25 mm, size of door frame section is of 105 x 60 mm with a rebate of 38 mm to accommodate 35 mm thick door shutter, with groove to insert gasket in the frame section, frame section filled with polyurethane foam, cut to length, and joined by way of welding, each frame provided with: a) 2mm thick MS powder coated butt hinges of 100 mm long – 3 Nos. for single shutter, 6 Nos. for double shutter. b) CRCA electroplates stiffeners of 6 Nos. – 3 in each vertical. c) 40 mm x 200 mm x 1.2 mm hold fasts screwed to stiffeners – 6 Nos with split end tail. d) Nylon Aldrops Receiver – 1 No. for single shutter frame. e)Tie Rod – 1 No Flush door shutters of 35mm thick solid bond wood blockboard type with commercial ply on both faces conforming to IS:2202 and Melamine Laminate Sheets of Mat Finish: 1.50mm thick on both sides, as per approved drawing, including the cost of 1 pair of dormakaba Antimicrobial pull handle TGDI-D 300 back to back with adjustable fixing for glass, wood and metal doors in satin stainless steel. The pull handles should have supporting washer with raised bevelling on the outer surface. Length =300mm, 22mm dia, -SS304 with Antimicrobial coating clear & transparent coating with protection tested for antibacterial activity as per ISO 22196 and against ISO 21702 proven to reduce viral loading on products and surfaces with up to 99.9% reduction/effectiveness or equivalent, 1 Nos of dormakaba rack and pinion door closer TS 68 EN size 2/3/4, with std. arm and with two independent closing valves and latching speed adjustable by arm. Silver finish. As per EN 1154. or equivalent, 1 set of dormakaba 706 dead lock and CR 6612 escutcheons with Euro Profile Double Cylinder with Both side Key Length = 60mm (30mm+30mm) Change Keys - 3 Nos.Finish - or equivalent, 1 nos of dormakaba lever action flush bolt with 19mm projecting bolt L=172 mm for wood door in satin chrome or equivalent, including cost of fixing the frame to the masonry / concrete, fixing the shutter to the frame, fixing the fixtures to the door, etc., cost of overheads and contractor's profit, etc. complete for finished item of work. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 20200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
64 | Providing and fixing factory made single extruded WPC (Wood Polymer Composite) solid door/window/Clerestory windows & other Frames/ Chowkhat comprising of virgin PVC polymer of K value 58-60 (Suspension Grade), calcium carbonate and natural fibers (wood powder/ rice husk/ wheat husk) and non toxic additives (maximum toxicity index of 12 for 100 gms) fabricated with miter joints after applying PVC solvent cement and screwed with full body threaded star headed SS screws having minimum frame density of 750 kg/cum, screw withdrawal strength of 2200 N (Face) & 1100 N (Edge), minimum compressive strength of 58 N/mm2, modulus of elasticity 900 N/mm2 and resistance to spread of flame of Class A category with property of being termite/borer proof, water/moisture proof and fire retardant and fixed in position with M.S hold fast/lugs/SS dash fasteners of required dia and length complete as per direction of Engineer-In- Charge. (M.S hold fast/lugs or SS dash fasteners shall be paid for separately). Note: For WPC solid door/window frames, minus 5 mm tolerance in dimensions i.e depth and width of profile shall be acceptable. Variation in profile dimensions on plus side shall be acceptable but no extra payment on this account shall be made. 26.86.1 Frame size 45 x 70 mm as per approved drawings/as directed by Engineering-in-Charge.
| a) For Toilet Frame size 45 x 70 mm | Rmt | 620 | 22 | 13640 | 0 | 0 | 5 | 3100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12400 | 0 | 0 |  |  | 0 | 0 | 47 | 29140
| b) For Building Door Frame Frame size 50 x 100/125 mm | Rmt | 832 | 10 | 8320 | 16 | 13312 | 36 | 29952 | 0 | 0 | 0 | 0 | 5 | 4160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 67 | 55744
65 | Providing and fixing factory made single extruded WPC (Wood Polymer Composite) solid decorative type flush door shutter of required size comprising of virgin polymer of K value 58-60 (Suspension Grade), calcium carbonate and natural fibers (wood powder/ rice husk/wheat husk) and non toxic additives (maximum toxicity index of 12 for 100 gms) having minimum density of 650 kg/cum and screw withdrawal strengthof 1800 N (Face) & 900 N (Edge), minimum compressive strength 50N/mm2, modulus of elasticity 850 N/mm2 and resistance to spread of flame of Class A category with property of being termite/borer proof, water/moisture proof and fire retardant. WPC to be laminated with PVC foil of minimum 14 microns thick of approved design pasted with hot melt adhesive on both faces of shutter and fixing with stainless steel butt hinges of required size with necessary full body threaded star headed counter sunk S.S screws, all as per direction of Engineer-In- Charge. including stainless steel butt hinges,Aldrops , Tower bolts, handles and necessary S.S screws as per approved drawings/as directed by Engineering-in-Charge.
| a) 30 mm thick For Toilet | Sqm | 4190 | 6 | 25140 | 0 | 0 | 2 | 8380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 25140 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 14 | 58660
| b) 35 mm thick For Building in Rooms | Sqm | 4860 | 4 | 19440 | 7 | 34020 | 15 | 72900 | 0 | 0 | 0 | 0 | 3 | 14580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 29 | 140940
66 | Providing and fixing factory made UPVC glazed/wire mesh windows/doors comprising of lead free UPVC multi-chambered frame, sash and mullion/coupler (where ever required) extruded profiles having minimum wall thickness of 1.70 mm for Series R1 and R2 profiles and 2.10 mm for Series R3 and R4 profiles conforming to EN: 12608 in any shape, colour and design duly reinforced with galvanized mild steel section made of required shape & size as per CPWD Specification, uPVC extruded glazing beads, interlocks and Inline sash adaptor (where ever required) of appropriate dimension, EPDM gasket, hardware, SS 304 grade fasteners of minimum 8 mm dia with countersunk head, comprising of matching polyamide PA6 grade sleeve for fixing frame to finished wall as per IS 1367 : Part 1 to 14, plastic packers, plastic caps and necessary stainless steel screws etc. Profile of frame, sash & mullion (if required) shall be mitred cut and fusion welded/mechanically jointed duly sealed at all corners, including drilling of holes for fixing hardware and drainage of water etc. After fixing frame the gap between frame and adjacent finished wall shall be filled with weather proof silicon sealant over backer rod of approved size and quality, all complete as per approved drawing conforming to CPWD specification & direction of Engineer-in-Charge. Section of steel reinforcement and cross sections of uPVC profiles to be as per design approved by Engineer-in-Charge. Wire mesh / Glazing of plain/ toughened/ laminated/ double glass unit with / without high performance coatings as per design requirements and conforming to IS: 3548 & IS: 16231 shall be paid separately. Note:- Structural design proof checked from a Government Engineering Institute, to be provided by the manufacturer for : (i) Sites with basic wind speed > 45 m/sec as per IS 875 – Part 3(ii) Sites with structure height more than 20m for all wind speeds Two track two panels Sliding window with Aluminium channel for roller track , wool pile, nylon rollers with SS 304 body Using R3 Series with frame ( 55mm & above) x (40mm & above ) & sash (30mm &above) x (55mm & above ) with Zinc alloy (Zmark) powder coated Handle on every Panel along with muti point locking System( Height upto 1.80 meter) as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 8054 | 11 | 88594 | 20 | 161080 | 19 | 153026 | 23 | 185242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 73 | 587942
67 | Providing and fixing UPVC Louver Fixed Ventilator Without mullion / transom , ventilator shutters and partitions etc. with Using R1 Series with frame (33mm & above ) x (35mm & Above ), Hegiht up to 0.90meter. complete as per the architectural drawings and the directions of engineer-in-charge as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 7542 | 8 | 60336 | 10 | 75420 | 10 | 75420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7542 | 0 | 0 |  |  | 0 | 0 | 29 | 218718
68 | Providing and fixing M.S. grills of required pattern in frames of windows etc., with M.S. flats, square or round bars etc. including priming coat with approved steel primer all complete. as per approved drawings/as directed by Engineering-in-Charge. | Kg | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| SUB HEAD - IX TOTAL AMOUNT |  |  |  | 215470 |  | 283832 |  | 342778 |  | 185242 |  | 0 |  | 18740 |  | 0 |  | 0 |  | 0 |  | 25140 |  | 19942 |  | 0 |  | 0 |  | 0
SUB HEAD -X ALUMINIUM WORKS
Fixed Glass Windows:-
69 | Providing and fixing of Aluminium Fixed Glass Windows as per the elevation drawings, fabricated out of heavy duty aluminium extruded profiles powder coated as per approved shade (55 + 5 micron) and specification with 6 mm clear toughened glassincluding providing Masking Tapes on the profiles for safety against external scratches at site
| The outer frame for the fixed glass windows will be made out of 63 x 38 x 2.00 mm thick box sections for both the Transoms and the mullions. The 6 mm thick clear toughened glass will be fitted with EPDM gasket and will be held in the frame using snap on slant glazing clips of size 17.3 x 19x 0.80 mm. The frame will be fitted to the masonry using appropriate grouting screws and will be fitted to plumb and water level. The entire periphery shall be sealed by application of approved weather silicone sealant (Wacker WN/Dow Corning 789 or equivalent) between the aluminium and masonry from the outside and paintable sealant (Wacker VS or Equivalent) from the inside to make the windows water tight. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 6480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
Door , Window, Ventilator & Partions :- Only Alluminium Work
Only Glazing:-
70 | Providing and fixing glazing in aluminium Louver, ventilator shutters and partitions etc. with EPDM rubber / neoprene gasket etc. complete as per the architectural drawings and the directions of engineer-in-charge . (Cost of aluminium snap beading shall be paid in basic item): With float glass panes of 8 mm thickness (weight not less than 20 kg/sqm) as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 1480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
Alluminium Frame , Partions & Particle Board:-
71 | Supply and Fixing in position alluminium powder coated glazed partitions using 5mm thick plain glass to full height using with prelaminated particle board of 12mm thick with decorative lamination on both sides, Grade I, Type II As per IS:12823 to a height of 0.9m at bottom panel and 1.2m height 5mm thick plain glass and above glass remaining height with 12mm thick prelaminated particle board with decorative lamination on both sides, Grade I, Type II As per IS:12823 and alluminium sections of size 37mm x62mm and 1.5mm thick with 1m C/C duly fixed with clip beading, pvc U beading on both sides including fixing the frame to Ceiling , Floor, concrete surfaces and walls by necessary Fittings of Ms Flats ,bolts and nuts and SS screws including cost and conveyance of all materials etc., complete as directed by engineer -in charge as per approved drawing. | Sqm | 7480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
72 | Supplying and Fixing Alluminium powder coated Door Consisting of Frame of Outer section Size 38.1x63.5x1.85mm, Shutter Frame of size 47.62x44.45x1.955mm thk,Lock Rail of Size 95.25x44.45x2 mm, and bottom rail of size 95.25x44.45x2mm thk,with hinges, tower bolts, door stopper, Godrej lock, handles, etc.,with lower panel 0.9m height prelaminated 12mm Thk both side decorative prelaminated patical board board truly exterior grade with 1.2m height 5.5mm thk. clear glass duly fixed with clip beading , PVC 'U' beading on both sides complete as per approved drawings for finished item of work at site and as per the directions complete as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 10450 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 62700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 6 | 62700
Alluminium Sliding Window :-
73 | Providing and fixing of Aluminium sliding Windows as per the elevation drawings, fabricated out of heavy duty aluminium extruded profiles powder coated as per approved shade (55 + 5 micron) and specification with 6 mm clear toughened glass including providing Masking Tapes on the profiles for safety against external scratches at site The 2 track sliding windows will have 2 shutters fitted with glass and 1 shutter fitted with Stainless Steel Mosquito Mesh. The fabrication of the sliding window shall be done with all the joints mitred. The Outer Frame and shutter corner joints will be held together with proprietary corner connecting mechanisms (without screws and L angles), thereby ensuring rigid and durable hairline joints. The glass panel will be held in place within the shutters using EPDM gaskets and appropriate profiles of woollen felt with fins shall be inserted between aluminiumframes/beadings and glass; as well as the felt being fitted on the inside of the periphery of the shutters, to make the shutters completely rattle free and air and water tight.The fixing shall be done at anchorage locations, in jambs, sills and heads by drilling holes with an electric drill, inserting PVC sleeves and the appropriate size of fasteners to provide the required anchoring in the masonry as per structural stability. The bottom frame section of the window will be provided with drain holes to allow rainwater collecting in the track to drain out. The entire periphery shall be sealed by application of approved weather silicone sealant(Wacker WN/Dow Corning 789 or equivalent) between the aluminium and masonry from the outside and paintable sealant (Wacker VS or Equivalent) from the inside to make the windows water tight. The windows will be fitted with all necessary accessories such as handles, heavy duty rollers, joint aligners, screw caps etc., As per existing windows specifications black powder coated are to be provided ,as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 9700 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
74 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm), with necessary accessories and screws etc. complete. as per approved drawings/as directed by Engineering-in-Charge. | Each | 1250 | 4 | 5000 | 6 | 7500 | 8 | 10000 | 3 | 3750 | 0 | 0 | 2 | 2500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 23 | 28750
| SUB HEAD - X TOTAL AMOUNT |  |  |  | 5000 |  | 7500 |  | 10000 |  | 66450 |  | 0 |  | 2500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
SUB HEAD -XI WATER PROOFING
75 | Terrace Water Proofing
| Surface Preparation: RCC Surfaces must be clean, even and sound concrete. Remove all oil, dirt, laitance and other Contaminants by manually. Grout: Providing Chemical injection treatment in the form of pressure grouting to the cold joint by injecting cement slurry mixed with grout admixture ArmGrout Additive @ 250 gms per bag of cement, in the required consistency through the pre fixed PVC nozzles in the 10mm dia holes, fixing of PVC nozzles with quick setting compound ReArm Fix 10S and final cutting the projected nozzles and sealing off the PVC nozzles after the injection operation is over with quick setting compound ReArm Fix 10S, non-shrink rapid setting mortar compound, finishing, curing etc. as per manufacturers specification and as directed. (including cement ). Application of Primer: Apply FloArm primer 1260 over well prepared surface. Application of Hybrid Polyurea waterproof coating: Application of Polyurethane waterproof coating of two component, spray applied fast setting coating based out of modified polyurethane/ Hybrid Polyurea Hybrid to achieve an elastic, high crack bridging waterproofing coating with long life expectancy waterproofing system AquaArm Purtech H 1 manufactured and supplied by MYK Arment or equivalent. AquaArm Purtech H1 can be applied at 1Kg/Sqm/mm thickness. The membrane will have the following technical parameters: Elongation : >500 % Recovery from 100 % Elongation : >85% Tensile Strength : >12 N/mm2 Applicator/ Agency has to submit 10 Years Guarantee on Bond Paper, MYK Arment make. | Sqm | 2040 | 79 | 161160 | 161 | 328440 | 228 | 465120 | 17 | 34680 | 0 | 0 | 99 | 201960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 32640 | 0 | 0 |  |  | 0 | 0 | 600 | 1224000
a) Providing and laying 150 Gsm Geo fabric membrane as separation layer
b) Protection Screed for Horizontal Areas: Providing and Laying M20 grade screed concrete in 1:100 to a minimum thickness of 75 mm mixed with AquaArm Proof WP10 -Integral Waterproofing admixture at the dosage of 125 ml/bag of cement and virgin polypropylene fibrated fiber at 0.9kg/m3 ,over waterproofing layer to a minimum thickness of 75 mm as per site requirement (Civil Contractor Scope) including control joints of 4M X 4M size and filling the panels with polyurethane sealant ( SealArm PU). Applicator/ Agency has to submit 10 Years Guarantee on Bond Paper, MYK Arment make
c) Protective Plaster: Applying avg. 15 mm thick, CM 1:4 plaster admixed with AquaArm Proof WP-10, Integral Waterproofing Compound @ 150 ml / bag of cement. (Mode of measurement will be actual treated area). (Including cement and sand cost and conveyance of all charges etc., ) Applicator/ Agency has to submit 10 Years Guarantee on Bond Paper, MYK Arment make
Note : Finally, testing the entire waterproofed area to check for its water tightness by ponding test duly providing guarantee against any leakage for 10 years.
76 | Waterproofing Treatment to RCC Wall For Sump & Septic Tanks
| Surface Preparation: (after de shuttering & curing) RCC Surfaces must be clean, even and sound concrete. Remove all oil, dirt, laitance and other Contaminants by manually. Construction joint treatment: Starter level lift joint, pour joints or critical joints in the wall make a “V” groove with 20mmx20mm width and depth. Fix the PVC Pipe of 10mm dia into the drilled hole and pack it tightly use quick setting cement - ReArmFix 10S. Packing the groove with non-shrink grout ArmGrout M65 Inject cementitious slurry by adding cement grout ArmGrout Additive maintaining W/P ratio of 0.45 with the dosage of 250gms/bag of cement under pressure through the nozzles. This should be applied before application of crystalline coating of AquaArm IC. including cemnet Providing and applying crystlline waterproofing treatment to RCC retaining wall. The waterproofing to be carried out using AquaArm IC of MYK Arment make, by preparing AquaArm IC slurry, by adding 6.75 to 8 liter clean water per 25 kg of AquaArm IC. Both the components should be mixed with a mechanical stirrer (300 to 700 RPM) until a lump free, homogeneous slurry is obtained. The slurry should be applied with a brush @ 1.5 kg/Sqm in two coats on the concrete substrate. The second coat should be applied when the first coat is still tacky. Applicator/ Agency has to submit 10 Years Guarantee on Bond Paper. | Sqm | 940 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 36660 | 0 | 0 | 0 | 0 | 55 | 51700 | 0 | 0 | 94 | 88360
| SUB HEAD - XI TOTAL AMOUNT |  |  |  | 161160 |  | 328440 |  | 465120 |  | 34680 |  | 0 |  | 201960 |  | 0 |  | 0 |  | 0 |  | 36660 |  | 32640 |  | 0 |  | 51700 |  | 0
SUBHEAD- XII: STRUCTURAL STEEL WORK :
77 | Providing and fixing roof covering precaoted coated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50mm (base metal of minimum 0.45mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required including scaffolding complete for finished item of work as per approved drawings/as directed by Engineering-in-Charge.
| POWDER COATED GALVANISED IRON PROFILE SHEET ( 60% Quantity of Material cost) | Sqm | 665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 54 | 35910
77(a) | fixing roof covering precaoted coated galvanised iron profile sheets (size, shape and pitch of corrugation as approved by Engineer-in-Charge) of total coated thickness 0.50mm (base metal of minimum 0.45mm thickness with total coating thickness of 0.05mm) with zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns. Sheet should have protective guard film of 25 microns minimum to avoid scratches during transportation and should be supplied in single length upto 12 metre or as desired by Engineer-in-charge. The sheet shall be fixed using self drilling /self tapping screws of size (5.5x 55 mm) with EPDM seal, complete upto any pitch in horizontal/ vertical or curved surfaces, excluding the cost of purlins, rafters and trusses and including cutting to size and shape wherever required including scaffolding complete for finished item of work as per approved drawings/as directed by Engineering-in-Charge. Material Supplied by VST. | Sqm | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 137500 | 0 | 0 | 1120.9 | 308247.5 | 0 | 0 | 31 | 8525 | 0 | 0 | 26 | 7150 | 0 | 0 |  |  |  | 0 | 1677.9 | 461422.5
78 | Providing & Cutting and Fabricating of Structural steel work riveted, bolted or welded in built up sections, Hollow Box Section , trusses ,vertical columns, baseplates, purlins, tie rods both nuts, washers, electrodes and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. as per approved drawings/as directed by Engineering-in-Charge. | Kgs | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2632 | 276360 | 0 | 0 | 38714.4 | 4065012 | 2875 | 301875 | 671 | 70455 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 44892.4 | 4713702
78(a) | Cutting and Fabricating of Structural steel work riveted, bolted or welded in built up sections, Hollow Box Section , trusses ,vertical columns, baseplates, purlins, tie rods both nuts, washers, electrodes and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. as per approved drawings/as directed by Engineering-in-Charge. ( Material Supplied By VST) | Kgs | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2233 | 71456 | 0 | 0 | 4060 | 129920 | 0 | 0 | 121 | 3872 | 0 | 0 | 114 | 3648 | 0 | 0 |  |  | 0 | 0 | 6528 | 208896
79 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required, In stringers, treads, landings etc. of stair cases, including use of 8mm Thick chequered plate wherever required, all complete. as per approved drawings/as directed by Engineering-in-Charge. | Kgs | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
80 | Providing and fixing 1mm thick M.S. sheet door with frame of 40x40x6 mm angle iron and 3 mm M.S. gusset plates at the junctions and corners, all necessary fittings complete, including applying a priming coat of approved steel primer. Using M.S. angels 40x40x6 mm for diagonal braces as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 6110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 177190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 29 | 177190
81 | Providing and fixing factory made ISI marked steel glazed doors, windows and ventilators, side /top /centre hung, with beading and all members such as F7D,F4B, K11 B and K12 B etc. complete of standard rolled steel sections, joints mitred and flash butt welded and sash bars tenoned and riveted, including providing and fixing of hinges, pivots, including priming coat of approved steel primer, but excluding the cost of other fittings, complete all as per approved design, (sectional weight of only steel members shall be measured for payment). Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) as per approved drawings/as directed by Engineering-in-Charge. | Kgs | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
82 | Providing and fixing MS hand railing made of Hollow tubes , Channels , Plates of approved size by welding etc. to be steel ladder railing, balcony railing, staircase railing and similar works, including applying priming coat of approved steel primer MS railing , cost and conveyance of all materials to site, all operational, incidental, labour charges etc., Complete for finished item of work as per approved drawings/as directed by Engineering-in-Charge. | Kgs | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 19000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 100 | 19000
83 | Providing and fixing stainless steel ( Grade 304) railing made of Hollow tubes, channels, plates etc. including welding, grinding, buffing, polishing and making curvature (wherever required) and fitting the same with necessary stainless steel nuts and bolts complete i/c fixing the railing with necessary accessories & stainless steel dash fasteners , stainless steel bolts etc., of required size, on the top of the floor or the side of waist slab with suitable arrangement as per approval of Engineer-in-charge. ( for payment purpose only weight of stainless steel members shall be considered excluding fixing accessories such as nuts, bolts, fasteners etc.) as per approved drawings/as directed by Engineering-in-Charge. | Kgs | 710 | 0 | 0 | 0 | 0 | 275 | 195250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 275 | 195250
84 | Providing and fixing in position MS foundation bolts of various diameters with machine turned threads , MS washers, nuts, and check nuts, anchoring and Base plates including grouting with cement concrete 1:1:2 (1 cement :1 sand :2 graded stone aggregate of 12.5mm down size ) etc., complete all as per approved drawings/as directed by Engineering-in-Charge. | Kgs | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 21128 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 6080 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 179 | 27208
85 | Providing and fixing precoated galvanised steel sheet roofing accessories 0.50 mm (+0.05 %) total coated thickness, Zinc coating 120 grams per sqm as per IS: 277, in 240 mpa steel grade, 5-7 microns epoxy primer on both side of the sheet and polyester top coat 15-18 microns using self drilling/ self tapping screws complete : Gutter (600 mm over all girth) complete all as per approved drawings/as directed by Engineering-in-Charge. | Rmt | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 36960 | 0 | 0 | 330 | 435600 | 17 | 22440 | 4 | 5280 | 0 | 0 | 12 | 15840 | 0 | 0 |  |  | 0 | 0 | 391 | 516120
| SUB HEAD - XII TOTAL AMOUNT |  |  |  | 0 |  | 0 |  | 195250 |  | 0 |  | 720594 |  | 0 |  | 4957779.5 |  | 360225 |  | 94212 |  | 0 |  | 26638 |  | 0 |  | 0 |  | 0
SUB HEAD -XIII APPROACH ROADS
86 | Preparation and consolidation of sub grade with power road roller of 8 to 12 tonne capacity after excavating earth to an average of 22.5 cm depth, dressing to camber and consolidating with road roller including making good the undulations etc. and re-rolling the sub grade and disposal of surplus earthwith lead upto 50 metres. | Sqm | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 508 | 96520 |  |  | 0 | 0 | 508 | 96520
87 | flooring for Road including groove cutting for transfer joint at every 4mts. Interval and filling with STP make PU based shali seal material. | Sqm | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 509 | 71260 |  |  | 0 | 0 | 509 | 71260
88 | Providing and laying at or near ground level factory made kerb stone of M-25 grade cement concrete in position to the required line, level and curvature, jointed with cement mortar 1:3 (1 cement: 3 coarse sand), including making joints with or without grooves (thickness of joints except at sharp curve shall not to more than 5mm), including making drainage opening wherever required complete etc. as per direction of Engineer-in-charge (length of finished kerb edging shall be measured for payment). (Precast C.C. kerb stone shall be approved drawings /as directed by Engineer-in-charge). Size - 600x150x450mm should be match with existing drain size | Cum | 9080 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 254240 |  |  | 0 | 0 | 28 | 254240
89 | Painting road surface marking with adequate nos of coats to give uniform finish with ready mixed road marking paint conforming to IS: 164, on bituminous surface in white/yellow shade, including cleaning the surface of all dirt, scales, oil, grease and foreign material etc. complete. New work (Two or more coats) as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221 | 57902 |  |  | 0 | 0 | 221 | 57902
90 | Providing and laying non-pressure NP2 class (light duty) R.C.C. pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 fine sand) including testing of joints etc. complete :
| a) 150 mm dia. R.C.C. pipe | Rmt | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 23500 |  |  | 0 | 0 | 50 | 23500
| b) 250 mm dia. R.C.C. pipe | Rmt | 742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 37100 |  |  | 0 | 0 | 50 | 37100
| c) 300 mm dia. R.C.C. pipe | Rmt | 885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 177000 |  |  | 0 | 0 | 200 | 177000
91 | Providing, laying and making kerb channel 15cm wide and 50 mm thick with cement concrete 1:3:6 (1 cement: 3 coarse sand:6 graded stone aggregate 20 mm nominal size) over 75mm bed of dry brick ballast 40 mm nominal size, well rammed and consolidated and grouted with fine sand, including finishing the top smooth etc. complete and as per direction of Engineer-in-charge. (Note: Saucer drain size should be match with existing drain size) | Sqm | 495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 27720 |  |  | 0 | 0 | 56 | 27720
| SUB HEAD - XIII TOTAL AMOUNT |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 745242 |  | 0 |  | 0
SUB HEAD -XIV SANITARY WORKS
92 | Supply, Laying,jointing & fixing in position under floor angaint wall in chases PVC SWR drainage pipe special of solvent cement joint of approved make conforming to IS: 13592 Type 'A' (4kg/sqcm) using lubricant as per manufacturer's specification, including cutting the pipes square to the required lenghts, necessary excavation. 75mm dia as per approved drawings/as directed by Engineering-in-Charge. | Rmt | 295 | 31 | 9145 | 0 | 0 | 18 | 5310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 7375 | 0 | 0 |  |  | 0 | 0 | 74 | 21830
93 | Supplying and laying, jointing and testing SWR 110MM DIA pipes of ISI make conforming to ISI 651 & 4127 with air tight cement joints in cm (1½:1) prop, including excavation of trenches and socket pits in any soils (except rock requiring blasting) up to 900mm (3') depth and refilling, watering and tamping, including cost and conveyance of all materials to site, all operational,incidental, labour charges, overheads and contractors profit, etc complete for finished item of work 110 mm (4") dia external as per approved drawings/as directed by Engineering-in-Charge. | Rmt | 685 | 34 | 23290 | 0 | 0 | 21 | 14385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 13700 | 0 | 0 | 15 | 10275 | 0 | 0 | 90 | 61650
94 | Supplying and laying, jointing and testing SWR 150mm Dia pipes of ISI make conforming to ISI 651 & 4127 with air tight cement joints in cm (1½:1) prop, including excavation of trenches and socket pits in any soils (except rock requiring blasting) up to 900mm (3') depth and refilling, watering and tamping, including cost and conveyance of all materials to site, all operational,incidental, labour charges, overheads and contractors profit, etc complete for finished item of work 150 mm (4") dia external as per approved drawings/as directed by Engineering-in-Charge. | Rmt | 980 | 50 | 49000 | 25 | 24500 | 25 | 24500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9800 | 651 | 637980 | 761 | 745780
95 | Providing and fixing white vitreous china pedestal type water closet (European type) with seat and lid, 10 litre low level white pvc dual flushing cistern & C.P. flush bend with fittings & C.I. brackets, 40 mm flush bend, overflow arrangement with specials of standard make and mosquito proof coupling of approved municipal design complete, including painting of fittings and brackets, cutting and making good the walls and floors wherever required : W.C. pan with ISI marked white solid plastic seat and lid as per approved drawings/as directed by Engineering-in-Charge.makes : HINDWARE ,P trap Size : 610x350x710mm Cat No. S1031111 , Flush Cat no. B1020105 , Carina Seat Cover Cat No. B1510101. | Each | 7580 | 2 | 15160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 15160 | 0 | 0 |  |  | 0 | 0 | 4 | 30320
96 | Providing and fixing single piece EWC with soft PP soft seat cover, Hinges,10 litre low level white vitreous china dual flushing cistern fixing accessories set and accessories such as angle stop valve and 450mm long braided hose with two 15mm nuts and rubber washers with nuts, cisterns fitting including cutting and making good the walls and floors where required.size 710x390x790mm,S-trap by Hindware ) etc. complete at all levels and heights for the finished item of work and as per approved drawings/as directed by Engineering-in-Charge.e.makes : HINDWARE S-trap 300mm cat no. S1013137 s-trap | Each | 31000 | 0 | 0 | 0 | 0 | 1 | 31000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1 | 31000
97 | Providing and fixing water closet squatting pan (Indian type W.C. pan ) with 100 mm sand cast Iron P or S trap, 10 litre low level white P.V.C. flushing cistern, including flush pipe, with manually controlled device (handle lever) conforming to IS : 7231, with all fittings and fixtures complete, including cutting and making good the walls and floors wherever required: White Vitreous china Orissa pattern W.C. pan of size 580x440 mm with integral type foot rests as per approved drawings/as directed by Engineering-in-Charge.make :Hindware
| Water closet squatting pan (Indian type W.C. pan ) | Each | 6290 | 2 | 12580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 2 | 12580
98 | Providing and fixing white vitreous china flat back half stall urinal of size 580x380x350mm with push cock, fittings, standard size C.P. brass flush pipe, spreaders with unions and clamps (all in C.P. brass) with waste fitting as per IS :2556, C.P. trap with outlet grating and other Couplings in C.P. brass, including painting of fittings and cutting and making good the walls and floors wherever required .Single half stall urinals with CP brass push cock ( by Hindware ) etc. complete at all levels and heights for the finished item of work and as per approved drawings/as directed by Engineering-in-Charge..make :Hindware
| white vitreous china flat back half stall urinal | Each | 11150 | 5 | 55750 | 0 | 0 | 1 | 11150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 22300 | 0 | 0 |  |  | 0 | 0 | 8 | 89200
99 | Providing and fixing of star white urinal partition of size 69 x 16.5 x 32.5CM Cat No. 61001 as per approved drawings/as directed by Engineering-in-Charge. Make: Hind ware or equivalent. | Each | 2900 | 4 | 11600 | 0 | 0 | 1 | 2900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5800 | 0 | 0 |  |  | 0 | 0 | 7 | 20300
100 | Providing, fixing, testing and commissioning of Paper holder with cover CAT NO: F880003 as per approved drawings/as directed by Engineering-in-Charge. By Hindware or equivalent. | Each | 1450 | 4 | 5800 | 0 | 0 | 1 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2900 | 0 | 0 |  |  | 0 | 0 | 7 | 10150
101 | Supply and fixing of floor trap of `P' or `S' type with Jali Cat No: NP1SPTNT110L Supreme as per approved drawings/as directed by Engineering-in-Charge. Make or equivalent. | Each | 290 | 2 | 580 | 0 | 0 | 1 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 580 | 0 | 0 |  |  | 0 | 0 | 5 | 1450
102 | Providing and fixing 15mm CP health faucet with 1.0 mtrs long tube with end nuts and hook and 1 nor 15mm CP brass angular stop cock with wall flange, Hook to be fixed with CP brass with suitable counter sunk screws, all of approved make etc., complete.with all fittings cp brass screws and fixtures complete, including cutting and making good the walls wherever required. ( Jaquar ) etc. complete at all levels and heights for the finished item of work and as per approved drawings/as directed by Engineering-in-Charge.make :JAQUAR
| Health Faucet | Each | 4350 | 4 | 17400 | 0 | 0 | 1 | 4350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8700 | 0 | 0 |  |  | 0 | 0 | 7 | 30450
103 | Supply and fixing of 50mm dia PVC 4 Kg/sqm Soil waste pipe, including bends, elbows, couplings, solvent etc complete as per approved drawings/as directed by Engineering-in-Charge. | Rm | 490 | 16 | 7840 | 2 | 980 | 13 | 6370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 5880 | 0 | 0 |  |  | 0 | 0 | 43 | 21070
104 | Supplying and fixing of 110mm dia Double Socket SWR pipes of 4 Kg/Sq cm and fixing all specials such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC clamps with required number of Bombay nails etc with solvent jointing as per standard practice including cost and conveance of all operational, incidental, labour charges, overheads & contractors profit etc. complete for finished item of work at all floor levels as per approved drawings/as directed by Engineering-in-Charge.
Internal PVC pipes
| PVC 4" | Each | 630 | 4 | 2520 | 0 | 0 | 2 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1260 | 0 | 0 |  |  | 0 | 0 | 8 | 5040
105 | Supplying and fixing of 75mm dia Double Socket SWR pipes of 4 Kg/Sq.cm and fixing all speicals such as plain bends, off sets, door bends, single junctions, double junctions as per site requirement, fixing with PVC, clamps with required number of Bombay nails etc with solvent jointing as per standard practice including cost and conveyance of all materials to site, all contractors profit etc. complete for finished item of work at all floor levels as per approved drawings/as directed by Engineering-in-Charge.
| PVC 3" | Each | 420 | 4 | 1680 | 0 | 0 | 2 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2100 | 0 | 0 |  |  | 0 | 0 | 11 | 4620
106 | Supplying and fixing of 110mm dia SWR pipe of 4kg/sqm for rain water down take pipes and fixing all specials such as plain bends, off sets fixing with PVC clamps with required number of Bombay nails etc with solvent jointing including cost and conveyance of all materials to site, all operational, incidental, labour charges etc., Complete for finished item of work. as per approved drawings/as directed by Engineering-in-Charge. | Rmt | 310 | 18 | 5580 | 44 | 13640 | 27 | 8370 | 8 | 2480 | 25 | 7750 | 12 | 3720 | 252 | 78120 | 16 | 4960 | 8 | 2480 | 10 | 3100 | 5 | 1550 | 0 | 0 |  |  | 0 | 0 | 425 | 131750
| SUB HEAD - XIV TOTAL AMOUNT |  |  |  | 217925 |  | 39120 |  | 112175 |  | 2480 |  | 7750 |  | 3720 |  | 78120 |  | 4960 |  | 2480 |  | 3100 |  | 87305 |  | 0 |  | 20075 |  | 637980
SUB HEAD -XV EXTERNAL SEWAGE SYSTEM
107 | Constructing brick masonry chamber for underground C.I. inspection chamber and bends with bricks in cement mortar 1:4 (1 cement : 4 coarse sand) C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover with frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg), R.C.C. top slab with 1:1.5:3 mix (1 cement : 1.5 fine sand : 3 graded stone aggregate 20 mm nominal size), foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand), finished smooth with a floating coat of neat cement on walls and bed concrete etc. complete as per standard design: Inside dimensions 500x700 mm and 45 cm deep for pipe line with one or two inlets : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5. as per approved drawings/as directed by Engineering-in-Charge. | Each | 7210 | 6 | 43260 | 6 | 43260 | 3 | 21630 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36050 | 0 | 0 | 0 | 0 |  |  | 10 | 72100 | 30 | 216300
108 | Constructing brick masonry circular manhole 1.22 m internal dia at bottom and 0.56 m dia at top in cement mortar 1:4 (1 cement :4 coarse sand) inside cement plaster 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement foundation concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) and making necessary channel in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) finished with a floating coat of neat cement, all complete as per standard design : 19.11.1 1.68 m deep with SFRC Cover and frame (heavy duty HD-20 grade designation) 560 mm internal diameter conforming to I.S. 12592, total weight of cover and frame to be not less than 182 kg. fixed in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) including centering, shuttering all complete. (Excavation, foot rests and 12 mm thick cement plaster at the external surface shall be paid for separately) : 19.11.1.1 With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 as per approved drawings/as directed by Engineering-in-Charge. | Each | 21980 | 24 | 527520 | 4 | 87920 | 6 | 131880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 36 | 791280 | 70 | 1538600
109 | Supply and Fixing of Septic Tank Cover of Size 600x600mm RCC Frame with cover Complete for finished item of work. | No.s | 2600 | 0 | 0 | 5 | 13000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5200 | 0 | 0 | 7 | 18200
110 | Supply and Fixing of Encapsuled PVC Steps Complete for finished item of wok. | No.s | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 5040 | 40 | 16800 | 52 | 21840
111 | Providing and fixing in position pre-cast R.C.C. drain cover and frame of required shape and approved quality Rectangular shape 600x450 mm internal dimensions | Each | 1190 | 5 | 5950 | 0 | 0 | 5 | 5950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5950 | 0 | 0 | 0 | 0 |  |  | 5 | 5950 | 20 | 23800
112 | Constructing brick masonry road gully chamber 45x45x77.5 cm with bricks in cement mortar 1:4 (1 cement : 4 coarse sand ) with precast R.C.C. vertical grating including top cover with frame complete as per standard design : With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 | Each | 5980 | 3 | 17940 | 1 | 5980 | 2 | 11960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 11960 | 0 | 0 |  |  | 0 | 0 | 8 | 47840
for all existing buildings
113 | Supply and fixing of sump cover with frame of size 600x600mm including cost and conveyance of all materials complete for finished item of work. | Each | 4150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 4 | 16600 | 4 | 16600
| SUB HEAD - XV TOTAL AMOUNT |  |  |  | 594670 |  | 150160 |  | 171420 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 42000 |  | 11960 |  | 0 |  | 10240 |  | 902730
SUB HEAD -XVI WATER SUPPLY SERVICES
114 | Providing and fixing White glazed vitreous Oval Wash Basin Under-Counter, size 570x480x210 mm., with supporting M.S. or C.I. Brackets, necessary pipe connection up to the outside face of the wall, having Telephonic Black / Colour Granite of 180 mm thick fixed on Black Kadappa Framework, Waste coupling 32 mm size full thread with 80 mm height Chrome plated, Bottle trap Chrome plated, Pillar Cock including necessary fittings with wall Flange etc. complete in all respects including cutting and making good the walls etc. complete as directed by Engineer in charge. Refer following product wise details/ Equivalent model of HINDWARE as per approved by engineer-in-charge. Wash Basin : Wash Basin : Wash Basin OVAL 570x 480 x 210 mm, Make : Hindware , Catl No.91008 Basin Mixer : Pillar cock , Make : JAQUAR, Model No.: FLR-CHR-5011NG Waste Coupling: Waste coupling (full thread) 32 mm, Model No.: F8050101, Make: CERA Bottle Trap : Bottle trap 300 mm (12”), Model No.: F8060401, Make: CERA
| Wash basins | Each | 9400 | 2 | 18800 | 1 | 9400 | 2 | 18800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 18800 | 0 | 0 |  |  | 0 | 0 | 7 | 65800
115 | Suppy and fixing indian make Flat back white Glazed wash hand basin 1st quality confirming to IS: 2556-Part-4 :1972 of Size 550x400mm Single C.P. Pillar cock as approved by engineeer in charge with waste fittings like rubber plug, chain, 32mm nominal size C.P. Fitting with parallel pipe thread confirming to IS:2963-1979 and fitted with 15mm nominal bore chromium plated pillar tap of 1st quality indian make 300grams SEICO/ESSO or Equivalent complete with standard CI Brackets including wooden block and painting to all iron fittings with 2 coats of synthetic enamel paint of approved colour and make including cutting the walls wherever necessary and making the same good for finished item of work, as per approved drawings/as directed by Engineering-in-Charge. Make: Hindware
| Wash Basins | Each | 8560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
116 | Providing and fixing 600x450 mm beveled edge mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | Sqm | 1480 | 2 | 2960 | 1 | 1480 | 2 | 2960 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2960 | 0 | 0 |  |  | 0 | 0 | 7 | 10360
117 | Providing & fixing C.P. brass towel ring fixed to rawl plug with C.P. brass screws. Refer following product wise details/ Equivalent model of as per approved drawings/as directed by Engineering-in-Charge. Cat No.ACN-1121N, Make : JAQUAR or Hind ware cat no F-880007 | Each | 1200 | 0 | 0 | 0 | 0 | 1 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2400 | 0 | 0 |  |  | 0 | 0 | 3 | 3600
118 | Providing and fixing C.P Soap Dispenser of best quality. Refer following product wise details/ Equivalent model of as per approved drawings/as directed by Engineering-in-Charge. Soap Dispenser : ,cat no. ACN-1131 Make : JAQUAR Basin Mixer : Pillar cock , Make : JAQUAR, Waste Coupling: Waste coupling (full thread) 32 mm, , Make : JAQUAR Bottle Trap : Bottle trap 300 mm (12”), , Make : JAQUAR | Each | 1450 | 0 | 0 | 0 | 0 | 1 | 1450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2900 | 0 | 0 |  |  | 0 | 0 | 3 | 4350
119 | Providing & Fixing in position C.P. 2-Way Bib Cock with Wall Flange of best quality complete in all respects including cutting and making good the walls etc. Refer following product wise details/ Equivalent model of JAQUAR, PARRYWARE as per approved drawings/as directed by Engineering-in-Charge.. 2 Way Bib Cock : Agate Pro Two way bib cock, Model No.: G3334A1, Make : PARRYWARE | Each | 2370 | 2 | 4740 | 0 | 0 | 1 | 2370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4740 | 0 | 0 |  |  | 0 | 0 | 5 | 11850
120 | Providing and fixing Long Body Bib Cock with Wall Flange best quality including cutting and making good the wall where required. Refer following product wise details/ Equivalent model of JAQUAR, as per approved drawings/as directed by Engineering-in-Charge. Long Body Bib cock : Coral Bib Cock with aerator, , Cat no. 5083NK Make : JAQUAR | Each | 1600 | 2 | 3200 | 0 | 0 | 1 | 1600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 3 | 4800
121 | Providing and fixing C.P. brass angle valve with wall flange complete, including cutting and making good the wall where required. Refer following product wise details/ Equivalent model of as per approved drawings/as directed by Engineering-in-Charge. Angle Valve : Star Angle valve, , Model No.: T9926A1, Make : PARRYWARE | Each | 1120 | 4 | 4480 | 1 | 1120 | 3 | 3360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6720 | 0 | 0 |  |  | 0 | 0 | 14 | 15680
122 | Providing and fixing of Bottle Trap of Cat No: F850015 Make: Hindware or equivalent. as per approved drawings/as directed by Engineering-in-Charge. | Each | 920 | 7 | 6440 | 1 | 920 | 2 | 1840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3680 | 0 | 0 |  |  | 0 | 0 | 14 | 12880
123 | Providing, fixing, testing and commissioning of Robe hook Cat. No.: F880004 By Hindware or equivalent. as per approved drawings/as directed by Engineering-in-Charge. | Each | 350 | 4 | 1400 | 0 | 0 | 1 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 700 | 0 | 0 |  |  | 0 | 0 | 7 | 2450
124 | Supplying & fixing PVC floor traps 1st quality ISI marked with C.P. Grating fixing with white cement as per site requirements with standard practice SS JALI nominal dia 100 mm (4") and grating size 100 mm dia of weight not less than 6 Kgs, including cost and conveyance of all materials to site, all operational,incidental , labour charges, overheads and contractor's profit, etc. complete for finished item of work. as per approved drawings/as directed by Engineering-in-Charge. | Each | 450 | 8 | 3600 | 1 | 450 | 1 | 450 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1800 | 0 | 0 |  |  | 0 | 0 | 14 | 6300
125 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints complete as per approved drawings/as directed by Engineering-in-Charge. Concealed work, including cutting chases and making grooves and finishing good the walls etc.
CPVC pipes
| 15 mm nominal dia Pipes | Rmt | 380 | 2 | 760 | 0 | 0 | 18 | 6840 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 20 | 7600
| 20 mm nominal dia Pipes | Rmt | 420 | 12 | 5040 | 0 | 0 | 3 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 15 | 6300
EXTERNAL
126 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings This includes jointing of pipes & fittings with one step CPVC solvent cement, trenching, refilling & testing of joints complete as per approved drawings/as directed by Engineering-in-Charge.
EXTERNAL
| 25 mm nominal dia Pipes | Rmt | 420 | 15 | 6300 | 35 | 14700 | 22 | 9240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 13440 | 0 | 0 |  |  | 0 | 0 | 104 | 43680
| 32 mm nominal dia Pipes | Rmt | 490 | 10 | 4900 | 0 | 0 | 8 | 3920 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 18 | 8820
| 40 mm nominal dia Pipes | Rmt | 530 | 0 | 0 | 0 | 0 | 10 | 5300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 10 | 5300
| 50 mm nominal dia Pipes | Rmt | 685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
127 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : as per approved drawings/as directed by Engineering-in-Charge. 25 mm dia nominal bore | Each | 620 | 2 | 1240 | 1 | 620 | 1 | 620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 620 | 0 | 0 |  |  | 5 | 3100 | 10 | 6200
| 32 mm dia nominal bore | Each | 680 | 1 | 680 | 0 | 0 | 1 | 680 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 680 | 0 | 0 |  |  | 3 | 2040 | 6 | 4080
| 40 mm dia nominal bore | Each | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 820 | 1 | 820
128 | Providing and fixing Stainless steel bib cock with wall flange of approved quality.Hindware Cat No: F200003 | Each | 490 | 4 | 1960 | 0 | 0 | 1 | 490 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 980 | 0 | 0 |  |  | 0 | 0 | 7 | 3430
129 | Providing and fixing C.P. brass stop cock (concealed) of Jaquar Concealed Stop Cock Suitable for 15mm Pipe Line with protection cap Cat No. ALD-CHR-083FT including exposed parts such as with Fitting Sleeve, Operating Lever & Adjustable Wall Flange with Seal etc., complete. | Each | 1075 | 6 | 6450 | 0 | 0 | 2 | 2150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2150 | 0 | 0 |  |  | 0 | 0 | 10 | 10750
130 | Providing and placing on terrace (at all floor levels) polyethylene water storage tank, ISI : 12701 marked, with cover and suitable locking arrangement and making necessary holes for inlet, outlet and overflow pipes but without fittings and the base support for tank. 500 Litres Capacity | No. | 8200 | 0 | 0 | 0 | 0 | 1 | 8200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1 | 8200
| 1000 Litres Capacity | No. | 14500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0
| 2000 Litres Capacity | No. | 25000 | 1 | 25000 | 1 | 25000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 25000 | 3 | 75000
131 | Providing and fixing square-mouth S.W. gully trap class SP-1 complete with C.I. grating brick masonry chamber with water tight C.I. cover with frame of 300 x 300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design:150 x 100 mm size P type 19.4.2.1 With common burnt clay F.P.S. (non modular) bricks of class designation 7.5 as per approved drawings/as directed by Engineering-in-Charge. | Each | 2600 | 2 | 5200 | 1 | 2600 | 2 | 5200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5200 | 0 | 0 |  |  | 0 | 0 | 7 | 18200
132 | S & F Bronze Ball valve with SS Ball and SS Spindle as per IS - Class - I, Indian make heavy type including cost and conveyance of all materials to site, all operational,incidental , labour charges, overheads and contractor's profit etc. complete for finished item of work in all floors as per approved drawings/as directed by Engineering-in-Charge.
| 20mm dia | Each | 750 | 1 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 1 | 750
| 25mm dia | Each | 1050 | 1 | 1050 | 0 | 0 | 1 | 1050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 187 | 196350 | 189 | 198450
| 30mm dia | Each | 1390 | 2 | 2780 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 2 | 2780
| 40mm dia | Each | 1785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 197 | 351645 | 197 | 351645
| 50mm dia | Each | 2350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 1 | 2350 | 1 | 2350
0
133 | Providing edge full moulding to 18 mm thick granite stone counters, Vanities etc., including machine polishing to edge to give high gloss finish etc. complete as as per approved drawings/as directed by Engineering-in-Charge. | Rmt | 415 | 5 | 2075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 5 | 2075
134 | Providing and fixing 18 mm thick gang saw granite cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills , facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. as per approved drawings/as directed by Engineering-in-Charge. | Sqm | 4200 | 3 | 12600 | 4 | 16800 | 4 | 16800 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 12600 | 0 | 0 |  |  | 0 | 0 | 14 | 58800
135 | Making connection of drain or sewer line with existing manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1 cement : 3 coarse sand), finished with a floating coat of neat cement and making necessary channels for the drain etc. complete as per approved drawings/as directed by Engineering-in-Charge.
| a) For pipes 100 to 250 mm diameter | No.s | 720 | 50 | 36000 | 50 | 36000 | 50 | 36000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 150 | 108000
| b) For pipes 250 to 300 mm diameter | No.s | 840 | 100 | 84000 | 100 | 84000 | 100 | 84000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 300 | 252000
| c) For pipes 350 to 450 mm diameter | No.s | 920 | 50 | 46000 | 50 | 46000 | 50 | 46000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 150 | 138000
| SUB HEAD - XVI TOTAL AMOUNT |  |  |  | 288405 |  | 239090 |  | 262130 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 80370 |  | 0 |  | 0 |  | 581305
Total Cost For Civil Works
[5 empty] | 4211952 |  | 5536662 |  | 6994523 |  | 872580 |  | 3784348 |  | 1802034 |  | 5035900 |  | 365185 |  | 338425 |  | 462303 |  | 709581 |  | 2755089 |  | 804332 |  | 4030065 |  | 37702978
| TOTAL AMOUNT | [31 empty] | 37702978
| Add : GST Extra @18% |  |  |  | 758151 |  | 996599 |  | 1259014 |  | 157064 |  | 681183 |  | 324366 |  | 906462 |  | 65733 |  | 60917 |  | 0 |  | 0 |  | 0 |  | 0 |  | 725412 |  | 6786536
| Grand Total |  |  |  | 4970103 |  | 6533261 |  | 8253537 |  | 1029644 |  | 4465531 |  | 2126400 |  | 5942362 |  | 430918 |  | 399342 |  | 462303 |  | 709581 |  | 2755089 |  | 804332 |  | 4755477 |  | 44489514
Say Rs. 4.45 Cr
42259048
COST SUMMARY
| SUB HEAD -I SITE CLEARANCE |  |  |  | 3798 |  | 5868 |  | 4644 |  | 49170 |  | 133605 |  | 0 |  | 0 |  | 0 |  | 3230 |  | 1998 |  | 6930 |  | 22512 |  | 3600 |  | 25050 |  | 260405
| SUB HEAD -II EARTHWORK & EXCAVATION |  |  |  | 99528 |  | 162760 |  | 169815 |  | 19917.2 |  | 54294 |  | 0 |  | 0 |  | 0 |  | 13111 |  | 71963 |  | 1620 |  | 573020 |  | 24480 |  | 191250 |  | 1381758.2
| SUB HEAD III - ANTI-TERMITE TREATMENT |  |  |  | 16560 |  | 33580 |  | 28060 |  | 3450 |  | 43700 |  | 0 |  | 0 |  | 0 |  | 2760 |  | 4600 |  | 0 |  | 0 |  | 0 |  | 0 |  | 132710
| SUB HEAD -IV PLAIN & REINFORCED CEMENT CONCRETE WORKS |  |  |  | 1432676 |  | 2596660 |  | 3193854 |  | 309540 |  | 1186060 |  | 739983 |  | 0 |  | 0 |  | 122368 |  | 276842 |  | 27291.8969 |  | 708715 |  | 637407 |  | 768750 |  | 12000146.8969
| SUB HEAD V - MASONARY WORK |  |  |  | 396680 |  | 660940 |  | 717640 |  | 74400 |  | 845820 |  | 233740 |  | 0 |  | 0 |  | 71840 |  | 0 |  | 86060 |  | 0 |  | 0 |  | 923000 |  | 4010120
| SUB HEAD VI - PLASTERING & SURFACE TREATMENT |  |  |  | 471864 |  | 717892 |  | 990380 |  | 95041 |  | 544517.5956 |  | 401535 |  | 0 |  | 0 |  | 10784 |  | 0 |  | 122232 |  | 0 |  | 29230 |  | 0 |  | 3383475.5956
| SUBHEAD-VII : FALSE CEILING : |  |  |  | 0 |  | 0 |  | 22680 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 49140 |  | 0 |  | 0 |  | 0 |  | 71820
| SUB HEAD -VIII FLOORINGS |  |  |  | 308216 |  | 310820 |  | 308577 |  | 32210 |  | 248007 |  | 199856 |  | 0 |  | 0 |  | 17640 |  | 0 |  | 157452 |  | 705600 |  | 27600 |  | 0 |  | 2315978
| SUB HEAD - IX JOINERY WORKS |  |  |  | 215470 |  | 283832 |  | 342778 |  | 185242 |  | 0 |  | 18740 |  | 0 |  | 0 |  | 0 |  | 25140 |  | 19942 |  | 0 |  | 0 |  | 0 |  | 1091144
| SUB HEAD -X ALUMINIUM WORKS |  |  |  | 5000 |  | 7500 |  | 10000 |  | 66450 |  | 0 |  | 2500 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 91450
| SUB HEAD -XI WATER PROOFING |  |  |  | 161160 |  | 328440 |  | 465120 |  | 34680 |  | 0 |  | 201960 |  | 0 |  | 0 |  | 0 |  | 36660 |  | 32640 |  | 0 |  | 51700 |  | 0 |  | 1312360
| SUBHEAD- XII: STRUCTURAL STEEL WORK : |  |  |  | 0 |  | 0 |  | 195250 |  | 0 |  | 720594 |  | 0 |  | 4957779.5 |  | 360225 |  | 94212 |  | 0 |  | 26638 |  | 0 |  | 0 |  | 0 |  | 6354698.5
| SUB HEAD -XIII APPROACH ROADS |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 745242 |  | 0 |  | 0 |  | 745242
| SUB HEAD -XIV SANITARY WORKS |  |  |  | 217925 |  | 39120 |  | 112175 |  | 2480 |  | 7750 |  | 3720 |  | 78120 |  | 4960 |  | 2480 |  | 3100 |  | 87305 |  | 0 |  | 20075 |  | 637980 |  | 1217190
| SUB HEAD -XV EXTERNAL SEWAGE SYSTEM |  |  |  | 594670 |  | 150160 |  | 171420 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 42000 |  | 11960 |  | 0 |  | 10240 |  | 902730 |  | 1883180
| SUB HEAD -XVI WATER SUPPLY SERVICES |  |  |  | 288405 |  | 239090 |  | 262130 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 80370 |  | 0 |  | 0 |  | 581305 |  | 1451300
| Total |  |  |  | 4211952 |  | 5536662 |  | 6994523 |  | 872580 |  | 3784348 |  | 1802034 |  | 5035900 |  | 365185 |  | 338425 |  | 462303 |  | 709581 |  | 2755089 |  | 804332 |  | 4030065 |  | 37702978
[5 empty] | 4211952 |  | 5536662 |  | 6994523 |  | 872580 |  | 3784348 |  | 1802034 |  | 5035900 |  | 365185 |  | 338425 |  | 462303 |  | 709581 |  | 2009847 |  | 804332 |  | 4030065 |  | 36957737
745241
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 745242 |  | 0 |  | 0 |  | 745241
0

## Rest Rooms & Toilet Dtl
PROPOSED CONSTRUCTION OF TOILET AND REST ROOM, TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Toilet and Rest Room
1 | Site levelling | 1 | 11.06 | 17.305 |  | 191.3933 | Sqm
[5 empty] | Total | 211 | Sqm
2 | Earth Work excavation
Under Footing
A) Upto 1.50 M
| F-1 | 8 | 2.2 | 2.2 | 1.5 | 58.08 | Cum
Under RR Masonry
| ALL Round Length | 1 | 36.19 | 0.75 | 0.7 | 18.9997 | Cum
| Total |  |  |  |  | 85 | Cum
Above 1.50 till 3.00 M
| F-1 | 8 | 2.2 | 2.2 | 1.5 | 58.08 | Cum
| Total |  |  |  |  | 64 | Cum
Above 3.00 till 4.50 M
| F-1 | 8 | 2.2 | 2.2 | 1 | 38.72 | Cum
| Total |  |  |  |  | 43 | Cum
| Total Quantity of Excavation |  |  |  |  | 192 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 192 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | -14 | Cum
| Sand Cohesion |  |  |  |  | -18 | Cum
| RCC Footing |  |  |  |  | -14 | Cum
| Below FFL Column |  |  |  |  | -4 | Cum
| Plinth Beam |  |  |  |  | -5 | Cum
| Below FFL RR Masonry |  |  |  |  | -18 | Cum
| Back fillingQty |  |  |  |  | 119 | Cum
| Basement Filling | 1 | 6.05 | 12 | 1 | 72.6 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | -1 | Cum
| Filling With Available Excavated Earth Considered |  |  |  |  | 192 | Cum
| Disposal of Excavated Earth |  |  |  |  | 0 | Cum
4 | PCC (1:4:8)
Under Footing
| F-1 | 8 | 2.1 | 2.1 | 0.1 | 3.528 | Cum
[5 empty] | Total | 3.8808 | Cum
Under RR Masonry
| ALL Round Length | 1 | 36.19 | 0.53 | 0.1 | 1.9181 | Cum
[5 empty] | Total | 2.1099 | Cum
Under Room PCC
| Rest Room | 1 | 6 | 8.045 | 0.1 | 4.827 | Cum
| Toilet Block | 1 | 6 | 3.955 | 0.1 | 2.373 | Cum
| Total |  |  |  | Total | 7.92 | Cum
| Total PCC quantity |  |  |  |  | 14 | Cum
5 | 230mm Thick Soling
Under Room
| Rest Room | 1 | 6 | 8.045 | 0.23 | 11.1021 | Cum
| Toilet Block | 1 | 6 | 3.955 | 0.23 | 5.4579 | Cum
[5 empty] | Total | 18 | Cum
6 | ATT
| Anti terminate | 1 | 6 | 12 |  | 72 | Sqm
[6 empty] | 72 | Sqm
| TOTAL ATT Qty. |  |  |  |  | 72 | Sqm
7 | RR MASONRY
Below NGL
| All Round Length | 1 | 36.19 | 0.38 | 0.6 | 8.2513 | Cum
[6 empty] | 9 | Cum
Above NGL
| All Round Length | 1 | 36.19 | 0.38 | 0.62 | 8.5264 | Cum
[6 empty] | 9 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 18 | Cum
8 | Plinth Protection
|  | 1 | 39 | 0.75 |  | 29 | Sqm
[6 empty] | 32 | Sqm
| Total Plinth Protection Qty. |  |  |  |  | 32 | Sqm
9 | R.C.C
a) | Under Footing
| F-1 | 8 | 1.9 | 1.9 | 0.45 | 12.996 | Cum
| Total footings RCC |  |  |  |  | 14 | Cum
b) | RCC Columns
Below FFL
| C1 | 8 | 0.23 | 0.45 | 4.07 | 3.37 | Cum
| Total columns RCC (upto FFL) |  |  |  |  | 4 | Cum
RCC for columns(above FFL upto GF)
| C1 | 8 | 0.23 | 0.45 | 3 | 2.484 | Cum
| Total |  |  |  |  | 3 | Cum
| Columns |  | RCC (upto FFL) |  |  | 4 | Cum
| Columns |  | Ground Floor |  |  | 3 | Cum
[5 empty] | TOTAL | 7 | Cum
c) | Plinth Beam
Horizontal Beams
| PB1 | 4 | 6.5 | 0.23 | 0.38 | 2.2724 | Cum
Vertical Beams
| PB2 | 2 | 12.035 | 0.23 | 0.38 | 2.1037 | Cum
| Total |  |  |  |  | 5 | Cum
d) | RCC FOR ROOF BEAMS
Ground Floor
Horizontal Beams
| RB1 | 4 | 6.5 | 0.23 | 0.45 | 2.691 | Cum
Vertical Beams
| RB2 | 2 | 12.035 | 0.23 | 0.45 | 2.4912 | Cum
| RB3 | 1 | 12.035 | 0.23 | 0.3 | 0.83042 | Cum
[5 empty] | Total | 7 | Cum
| Roof Beams |  | Ground Floor |  | TOTAL | 7 | Cum
e) | Roof Slab
GROUND FLOOR
| Slab-1 | 1 | 6.05 | 12.035 | 0.125 | 9.1015 | Cum
Cum
[6 empty] | 10 | Cum
| Slabs |  | Ground Floor |  | TOTAL | 10 | Cum
f) | Lintels
|  | 3 | 6.5 | 0.23 | 0.3 | 1.3455 | Cum
|  | 2 | 12.035 | 0.23 | 0.3 | 1.6608 | Cum
| Lintels |  | Ground Floor |  | TOTAL | 4 | Cum
g) | CHAJJA's
|  | 2 | 6.5 | 0.6 | 0.075 | 0.585 | Cum
|  | 2 | 13.235 | 0.6 | 0.075 | 1.1911
[6 empty] | 2 | Cum
| Chajja's |  | Ground Floor |  | TOTAL | 2 | Cum
RCC Concrete Work
| Total Rcc Qty. All Works Upto Plinth Level. |  |  |  |  | 23 | Cum
| Total Rcc Qty. All Works Above Plinth upto Floor V Level |  |  |  |  | 20 | Cum
| Chajja's&Lintel |  |  |  |  | 6 | Cum
|  |  |  | Grand Total |  | 49 | Cum
10 | Supplying & Fabrication of Reinforcement steel
| Footings- 60 kg/cum |  | 14 | X | 60 | 840 | kg
| Plinth Beam- 150 kg/cum |  | 5 | X | 150 | 750 | kg
| Columns-250 kgs/cum |  | 7 | X | 250 | 1750 | kg
| Roof beams-250 kgs/cum |  | 7 | X | 250 | 1750 | kg
| Slabs-80 kgs/cum |  | 10 | X | 80 | 800 | kg
| Stair case-100 kgs/cum |  | 0 | X | 100 | 0 | kg
| Lintels etc., -80 kg/cum |  | 4 | X | 80 | 320 | kg
| Chajjas etc., -60 kg/cum |  | 2 | X | 60 | 120 | kg
|  |  | 49 |  |  | 6330 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 317 | kg
[6 empty] | 6647 | KG
[5 empty] | (or) | 7 | MT
11 | SHUTTERING
Under Footing
| F-1 | 8 | 7.6 |  | 0.45 | 27.36 | Sqm
| Total Foundation Shuttering |  |  |  |  | 30 | Sqm
RCC Columns
Below FFL
| C1 | 8 | 1.36 |  | 4.07 | 44.2816 | Sqm
[6 empty] | 49 | Sqm
RCC for columns(above FFL upto GF)
| C1 | 8 | 1.36 |  | 3 | 32.64 | Sqm
[6 empty] | 36 | Sqm
| Columns Shuttering |  | Up to Floor FFL |  |  | 49 | Sqm
| Columns Shuttering |  | Ground Floor |  |  | 36 | Sqm
[5 empty] | Total | 85 | Sqm
Shuttering For Plinth Beam
Horizontal Beams
| PB1 | 4 | 6.5 |  | 0.76 | 19.76 | Sqm
Vertical Beams
| PB2 | 2 | 12.035 |  | 0.76 | 18.2932 | Sqm
[6 empty] | 42 | Sqm
Shuttering For Roof Beams
Ground Floor
Horizontal Beams
| RB1 | 4 | 6.5 |  | 1.13 | 29.38 | Sqm
Vertical Beams
| RB2 | 2 | 12.035 |  | 1.13 | 27.1991 | Sqm
| RB3 | 1 | 12.035 |  | 0.83 | 9.989 | Sqm
[6 empty] | 73 | Sqm
| Roof Beams Shuttering |  | Ground Floor |  |  | 73 | Sqm
Shuttering For Roof Slab
GROUND FLOOR
| Slab-1 | 1 | 6.05 | 12.035 |  | 72.8118 | Sqm
|  | 1 | 36.17 |  | 0.125 | 4.5213 | Sqm
|  |  |  | Total |  | 85 | Sqm
| Shuttering for Slabs |  | Ground Floor |  |  | 85 | Sqm
Shuttering for Lintels
|  | 3 | 6.5 | 0.23 |  | 4.485 | Sqm
|  | 3 | 6.5 |  | 0.6 | 11.7 | Sqm
|  | 2 | 12.035 | 0.23 |  | 5.5361 | Sqm
|  | 2 | 12.035 |  | 0.6 | 14.442 | Sqm
[5 empty] | Total | 40 | Sqm
Shuttering for Chajjas
| Bottom | 2 | 6.5 | 0.6 |  | 7.8 | Sqm
|  | 2 | 13.235 | 0.6 |  | 15.882 | Sqm
| Sides | 2 | 7.7 |  | 0.08 | 1.232 | Sqm
|  | 2 | 13.235 |  | 0.08 | 2.1176 | Sqm
[5 empty] | Total | 30 | Sqm
12 | Brick Work
CC- Block Brick Work
Ground Floor
| Horizontal | 3 | 6.5 | 0.2 | 2.7 | 10.53 | Cum
| Vertical | 2 | 12 | 0.2 | 2.7 | 12.96 | Cum
STEPS
| Entrance Steps 1&2 | 2 | 2.1 | 0.9 | 0.2 | 0.756 | Cum
|  | 2 | 2.1 | 0.6 | 0.4 | 1.008 | Cum
|  | 2 | 2.1 | 0.3 | 0.6 | 0.756 | Cum
Deductions
| D2 | 2 | 0.9 | 0.2 | 2.1 | -0.756 | Cum
| W2 | 6 | 1.2 | 0.2 | 1.2 | -1.728 | Cum
| V1 | 6 | 0.9 | 0.2 | 0.6 | -0.648 | Cum
| Total 200 mm brick work quantity |  |  |  |  | 25 | Cum
| 200mm Thick Brick Work |  | Ground Floor |  | TOTAL | 25 | Cum
13 | Half brick masonry
Ground Floor
Toilet Block
| WC | 3 | 3.025 |  | 2.885 | 26.1814 | Sqm
| WC | 1 | 1.325 |  | 2.885 | 3.8226 | Sqm
| Urinal Partion Wall | 1 | 0.9 |  | 2.1 | 1.89 | Sqm
| Parapet Wall | 1 | 36 |  | 0.9 | 32.4 | Sqm
Deductions
| D4 | 4 | 0.75 | 0.2 | 2.1 | -1.26 | Cum
| Total 100 mm brick work quantity |  |  |  |  | 69 | Sqm
| 100 mm Brick Work |  | Ground Floor |  | TOTAL | 69 | Sqm
14 | Plastering
External plastering(20mm)
Ground Floor
| All round | 1 | 36 |  | 4.6 | 165.6 | Sqm
| Parapet Wall Plastering | 1 | 36 |  | 1.915 | 68.94 | Sqm
Entrance Steps -1&2
| Sides | 4 | 0.9 |  | 0.6 | 2.16 | Sqm
Deductions of 50% External
| D2 | 1 | 0.9 |  | 2.1 | -1.89 | Sqm
| W2 | 3 | 1.2 |  | 1.2 | -4.32 | Sqm
| V1 | 3 | 0.9 |  | 0.6 | -1.62 | Sqm
[5 empty] | Total | 252 | Sqm
| External plastering |  | Ground Floor |  |  | 252 | Sqm
15 | Internal plastering(15mm)
Ground Floor
| Rest Room | 1 | 26.49 |  | 3.6 | 95.364 | Sqm
| Toilet Block | 1 | 15.51 |  | 3.6 | 55.836 | Sqm
| Urinal Partion Wall Plastering | 1 | 1.8 |  | 2.1 | 3.78 | Sqm
| WC | 4 | 5.4 |  | 2.885 | 62.316 | Sqm
Deductions of 50% Internal
| D2 | 1 | 0.9 |  | 2.1 | -1.89 | Sqm
| D4 | 4 | 0.75 |  | 2.1 | -6.3 | Sqm
| W2 | 3 | 1.2 |  | 1.5 | -5.4 | Sqm
| V1 | 3 | 0.9 |  | 0.6 | -1.62 | Sqm
[5 empty] | Total | 222 | Sqm
| Internal plastering |  | Ground Floor |  | TOTAL | 222 | Sqm
16 | Ceiling plastering
Ground Floor
| Rest Room | 1 | 5.6 | 7.645 |  | 42.812 | Sqm
| Toilet Block | 1 | 5.6 | 3.755 |  | 21.028 | Sqm
| Open Beams | 1 | 18 |  | 0.83 | 14.94 | Sqm
Chajja's Plaastering
| Bottom | 4 | 6.5 | 0.6 |  | 15.6 | Sqm
|  | 4 | 13.235 | 0.6 |  | 31.764
| Sides | 2 | 7.7 |  | 0.08 | 1.232 | Sqm
|  | 2 | 13.235 |  | 0.08 | 2.1176
[6 empty] | 142 | Sqm
| Ceiling plastering |  | Ground Floor |  | TOTAL | 142 | Sqm
17 | Pointing on stone work
Above NGL
| All Round Length | 1 | 0 |  | 0 | 0 | Sqm
[6 empty] | 0 | Sqm
| Pointing Work |  |  |  | TOTAL | 0 | Sqm
18 | Plaster drip course/water patti
| Bottom | 1 | 41.88 |  |  | 41.88 | Rmt
| Parapet Wall Watter Patti | 1 | 36 |  |  | 36 | Rmt
[5 empty] | Total | 86 | Rmt
19 | Flooring
Vitrified Floor Tiles
Ground Floor
| Rest Room | 1 | 5.6 | 7.645 |  | 42.812 | Sqm
[5 empty] | Total | 47 | Sqm
| Vitrified Flooring |  | Ground Floor |  | TOTAL | 47 | Sqm
20 | Skirting
| Rest Room | 1 | 26.49 |  | 0.1 | 2.649 | Sqm
| Vitrified Flooring Skirting |  |  |  | Total | 3 | Sqm
21 | Non skid ceramic tiles in toilets
Ground Floor
| Toilet Block | 1 | 5.6 | 2.155 |  | 12.068 | Sqm
| wc | 4 | 1.2 | 1.5 |  | 7.2 | Sqm
[5 empty] | Total | 21 | Sqm
| Non-skid Flooring |  | Ground Floor |  | TOTAL | 21 | Sqm
22 | Dadoing
Ground Floor
| Toilet Block | 1 | 15.51 |  | 3.6 | 55.836 | Sqm
| Urinal Partion Wall Plastering | 1 | 1.8 |  | 3.6 | 6.48 | Sqm
| WC | 4 | 5.4 |  | 3 | 64.8 | Sqm
Deductions
| D4 | 4 | 0.75 |  | 2.1 | -6.3 | Sqm
[5 empty] | Total | 133 | Sqm
| Dadoing |  | Ground Floor |  | TOTAL | 133 | Sqm
23 | Kota Stone Flooring
Entrance Steps - 1&2
| Threads | 6 | 2 | 0.3 |  | 3.6 | Cum
| Raiser | 6 | 2 |  | 0.2 | 2.4 | Cum
[5 empty] | Total | 7 | Sqm
| Kota Stone Flooring |  | Ground Floor |  | TOTAL | 7 | Sqm
24 | 18mm thick gang saw cut mirror polished
Toilet Block
| Wash Basin | 1 | 2.05 | 0.6 |  | 1.23 | Sqm
[5 empty] | Total | 1 | Sqm
Doors & Window Sills
| D2 | 1 | 0.9 | 0.2 |  | 0.18 | Sqm
| W2 | 6 | 1.2 | 0.2 |  | 1.44 | Sqm
[5 empty] | Total | 2 | Sqm
|  |  |  | Grand Total |  | 3 | Sqm
25 | Painting
| External painting |  |  | Ground Floor |  | 252 | Sqm
| Internal painting |  |  | Ground Floor |  | 364 | Sqm
| Internal&External Paint With White Cement Based Putty |  |  | Ground Floor |  | 616 | Sqm
| Ceiling painting - White wash |  |  | Ground Floor |  | 0 | Sqm
26 | Water Proofing works
Ground Floor
Toilet Waterproofing
| Toilet Block | 1 | 5.6 | 3.755 |  | 21.028 | Sqm
[5 empty] | Total | 23 | Sqm
Terrace Water Proofing
| Terrace | 1 | 6 | 12 |  | 72 | Sqm
[5 empty] | Total | 79 | Sqm
27 | Joinery
Ground Floor
WPC Door Shutter 35mm Thick
| D2 | 2 | 0.9 |  | 2.1 | 3.78 | Sqm
[6 empty] | 4 | Sqm
| shutters |  |  |  | Total | 4 | Sqm
b) WPC Door Frame
Ground Floor
| D2 | 2 | 5.1 |  |  | 10.2 | Rmt
[6 empty] | 10 | Rmt
| WPC Door Frames |  |  |  | TOTAL | 10 | Rmt
28 | WPC Door Shutter 30mm Thick Toilet Door
| D4 (TD) | 4 | 0.75 |  | 2.1 | 6.3 | Sqm
[6 empty] | 6 | Sqm
| WPC Door Shutter 30mm Thick |  |  |  | Total | 6 | Sqm
WPC Door Frame
| D4 (TD) | 4 | 4.95 |  |  | 19.8 | Rmt
[5 empty] | Total | 22 | Rmt
29 | UPVC Window
Ground Floor
Upvc Windows & Ventilator
| W2 | 6 | 1.2 |  | 1.5 | 10.8 | Sqm
[5 empty] | Total | 11 | Sqm
| UPVC Sliding Window |  |  |  | Total | 11 | Sqm
30 | Ventilators Louvers
| V1 | 6 | 0.9 |  | 0.6 | 3.24 | Sqm
|  | 6 | 1.2 |  | 0.6 | 4.32 | Sqm
[6 empty] | 8 | Sqm
| Ventilators |  |  |  | Total | 8 | Sqm
31 | Hydraulic Door Closer
| D2 | 4 |  |  |  | 4 | No's
[6 empty] | 4 | No's
32 | MS Grills For Windows
| MS Grills 20kg/Sqm | 0 | 0 |  |  | 0 | KGS
| Convertion (20kg/Sqm) |  |  |  |  | 0 | KGS
33 | Synthatic Enamel Paint
a) Steel surfaces with zinc chromate primer
Windows For MS Grill
| W2 | 0 | 0 |  | 0 | 0 | Sqm
[5 empty] | Total | 0 | Sqm
b) Wooden surface with approved primer
| D2 | 1 | 0.9 |  | 2.4 | 2.16 | Sqm
| D4 | 5 | 0.75 |  | 2.1 | 7.875 | Sqm
[5 empty] | Total | 11 | Sqm
[5 empty] | Grand Total | 11 | Sqm
SEWAGE
1 | Indian type W.C. pan
| Toilet Block WC | 1 | 2 |  |  | 2 | Nos
| Total Qty. |  |  |  |  | 2 | Nos
2 | European type
| Toilet Block WC | 1 | 2 |  |  | 2 | Nos
| Total Qty. |  |  |  |  | 2 | Nos
3 | Urinals
| Toilet Block | 1 | 5 |  |  | 5
| Total Qty |  |  |  |  | 5 | Nos
4 | Urinal Partitions
| Toilet Block | 4 |  |  |  | 4
| Total Qty |  |  |  |  | 4 | Nos
5 | Paper holder
| Toilet Block | 1 | 4 |  |  | 4
| Total Qty |  |  |  |  | 4 | Nos
6 | Health Faucet
| Toilet Block WC | 1 | 4 |  |  | 4
| Total Qty |  |  |  |  | 4 | Nos
7 | S.W. gully trap
|  | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
8 | Gully chamber
|  | 1 | 3 |  |  | 3
| Total Qty |  |  |  |  | 3 | Nos
9 | P or S Trap
| Toilet Block WC | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
10 | Inspection Chamber
| IC 450 x 600 mm | 1 | 6 |  |  | 6
| Total Qty |  |  |  |  | 6 | Nos
11 | Manhole
| 500mm Dia Top and 1200mm Dia Bottom | 12 | 2 |  |  | 24
| Total Qty |  |  |  |  | 24 | Nos
12 | Soil Pipe
a) | 50mmØ SWR /PVC WASTE Water PIPE | 1 | 15.645 |  |  | 15.645 | Rmt
[6 empty] | 16 | Rmt
b) | 75mmØ SWR /PVC WASTE Water PIPE | 1 | 30.645 |  |  | 30.645 | Rmt
[6 empty] | 31 | Rmt
c) | 75mmØ SWR /PVC WASTE Water PIPE
|  | 1 | 4 |  |  | 4
[6 empty] | 4 | Nos
c) | 110mmØ SWR /PVC SOIL WASTE PIPE | 1 | 34 |  |  | 34 | Rmt
[6 empty] | 34 | Rmt
d) | 110mmØ SWR /PVC WASTE Water PIPE
|  | 1 | 4 |  |  | 4
[6 empty] | 4 | Nos
f) | 150mmØ SWR /PVC SOIL WASTE PIPE | 1 | 50 |  |  | 50 | Rmt
[6 empty] | 50 | Rmt
13 | Rain water down take pipes
| 110mm Dia | 4 | 4.5 |  |  | 18 | Rmt
[5 empty] | Total | 18 | Rmt
WATER SUPPLY
14 | WASH BASINS
| Toilet Block | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
15 | Bottle Trap
| Toilet Block | 1 | 7 |  |  | 7
| Total Qty |  |  |  |  | 7 | Nos
16 | Floor Trap
| Toilet Block | 1 | 8 |  |  | 8
| Total Qty |  |  |  |  | 8 | Nos
17 | Two Way Bib Cock
| Toilet Block | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
18 | Long Body Bib Cock
| Toilet Block | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
19 | Stop Cock
| Toilet Block | 1 | 6 |  |  | 6
| Total Qty |  |  |  |  | 6 | Nos
20 | Mirror Glass
| Toilet Block | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
21 | Towel Ring
| Toilet Block | 1 | 0 |  |  | 0
| Total Qty |  |  |  |  | 0 | Nos
22 | Soap Dish
| Toilet Block | 1 | 0 |  |  | 0
| Total Qty |  |  |  |  | 0 | Nos
23 | Double Towel Bar
| Toilet Block | 1 | 0 |  |  | 0
| Total Qty |  |  |  |  | 0 | Nos
24 | Robe Hook
| Toilet Block | 1 | 4 |  |  | 4
| Total Qty |  |  |  |  | 4 | Nos
25 | Angle Valve
| Toilet Block | 1 | 4 |  |  | 4
| Total Qty |  |  |  |  | 4 | Nos
26 | Stain Less Steel Bib Cock
| Toilet Block | 1 | 4 |  |  | 4
| Total Qty |  |  |  |  | 4 | Nos
27 | 15mmØ CPVC Line | 1 | 1.8 |  |  | 1.8 | Rmt
[6 empty] | 2 | Rmt
28 | 20mmØ CPVC Line | 1 | 12 |  |  | 12 | Rmt
[6 empty] | 12 | Rmt
29 | 25mmØ CPVC Line | 1 | 9.8 |  |  | 9.8 | Rmt
[6 empty] | 10 | Rmt
30 | 32mmØ CPVC Line | 1 | 5 |  |  | 5 | Rmt
[6 empty] | 5 | Rmt
31 | 32mmØ CPVC Down Take Pipe | 1 | 4.5 |  |  | 4.5 | Rmt
[6 empty] | 5 | Rmt
[5 empty] | Total | 10 | Rmt
32 | 25mmØ CPVC UP Take Pipe | 1 | 4.5 |  |  | 4.5 | Rmt
[6 empty] | 5 | Rmt
[5 empty] | Total | 15 | Rmt
33 | Gate Valve
| 25mm dia | 1 | 2 |  |  | 2
| 32mm dia | 1 | 1 |  |  | 1
[6 empty] | 3 | Nos
34 | Bronze Ball valve with SS Ball
| 32mm dia | 1 | 2 |  |  | 2
[6 empty] | 2 | Nos
35 | Syntex Tank
| 1500 Liter Capacity | 1 | 1 |  |  | 1
[6 empty] | 1 | Nos

## Workers rest room&change room
PROPOSED CONSTRUCTION OF WORKERS REST ROOM AND CHANGE ROOM , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Worker's Rest Room & Change Room
1 | Site levelling | 1 | 19.66 | 15.06 |  | 296.0796 | Sqm
[5 empty] | Total | 326 | Sqm
2 | Earth Work excavation
A) Upto 1.50 M
| F-1 | 15 | 2.1 | 2.1 | 1.5 | 99.225 | Cum
Under RR Masonry
| ALL Round Length | 1 | 49.44 | 0.75 | 0.7 | 25.956 | Cum
| Total |  |  |  |  | 138 | Cum
Above 1.50 till 3.00 M
| F-1 | 15 | 2.1 | 2.1 | 1.5 | 99.225 | Cum
| Total |  |  |  |  | 109 | Cum
Above 3.00 till 4.50 M
| 0 | 15 | 2.1 | 2.1 | 1 | 66.15 | Cum
| Total |  |  |  |  | 73 | Cum
| Total Quantity of Excavation |  |  |  |  | 320 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 320 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | -27 | Cum
| Sand Cohesion |  |  |  |  | -37 | Cum
| RCC Footing |  |  |  |  | -24 | Cum
| Below FFL Column |  |  |  |  | -7 | Cum
| Plinth Beam |  |  |  |  | -7 | Cum
| Below FFL RR Masonry |  |  |  |  | -28 | Cum
| Back fillingQty |  |  |  |  | 190 | Cum
| Basement Filling | 1 | 14.6 | 10 | 1 | 146 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | 16 | Cum
| Filling With Available Excavated Earth Considered |  |  |  |  | 320 | Cum
| Disposal of Excavated Earth |  |  |  |  | 0 | Cum
4 | PCC (1:4:8)
Under Footing
| F-1 | 15 | 2.1 | 2.1 | 0.1 | 6.615 | Cum
[5 empty] | Total | 7.2765 | Cum
Under RR Masonry
| ALL Round Length | 1 | 49.44 | 0.6 | 0.1 | 2.9664 | Cum
[5 empty] | Total | 3.263 | Cum
Under Room PCC
| Workers Rest Room & Change Room | 1 | 14.66 | 10.06 | 0.1 | 14.748 | Cum
| Total |  |  |  | Total | 16.2228 | Cum
| Total PCC quantity |  |  |  |  | 27 | Cum
5 | 230mm Thick Soling
Under Room
| Workers Rest Room & Change Room | 1 | 14.6 | 10.06 | 0.23 | 33.7815 | Cum
[5 empty] | Total | 37 | Cum
6 | ATT
| Anti terminate | 1 | 14.6 | 10 |  | 146 | Sqm
[6 empty] | 146 | Sqm
| TOTAL ATT Qty. |  |  |  |  | 146 | Sqm
7 | RR MASONRY
Under RR Masonry
Below FGL
| All Round Length | 1 | 49.44 | 0.45 | 0.6 | 13.3488 | Cum
[6 empty] | 15 | Cum
Above NGL
| All Round Length | 1 | 49.44 | 0.38 | 0.62 | 11.6481 | Cum
[6 empty] | 13 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 28 | Cum
8 | Plinth Protection
|  | 1 | 52.2 | 0.75 |  | 39 | Sqm
[6 empty] | 43 | Sqm
| Total Plinth Protection Qty. |  |  |  |  | 43 | Sqm
9 | R.C.C
a) | Under Footing
| F-1 | 15 | 1.8 | 1.8 | 0.45 | 21.87 | Cum
| Total footings RCC |  |  |  |  | 24 | Cum
b) | RCC Columns
GROUND FLOOR
Below FFL
| C1 | 15 | 0.23 | 0.45 | 4.07 | 6.3187 | Cum
| Total columns RCC (upto FFL) |  |  |  |  | 7 | Cum
RCC for columns(above FFL upto GF)
| C1 | 15 | 0.23 | 0.45 | 4.2 | 6.5205 | Cum
| Total |  |  |  |  | 7 | Cum
| Columns |  | RCC (upto FFL) |  |  | 7 | Cum
| Columns | Ground Floor (Above FFL) |  |  |  | 7 | Cum
[5 empty] | TOTAL | 14 | Cum
c) | Plinth Beam
Horizontal Beams
| PB1 | 3 | 14.66 | 0.23 | 0.38 | 3.8439 | Cum
Vertical Beams
| PB2 | 3 | 10.06 | 0.23 | 0.38 | 2.6377 | Cum
| Total |  |  |  |  | 7 | Cum
d) | RCC FOR ROOF BEAMS
Ground Floor
Horizontal Beams
| RB1 | 3 | 14.6 | 0.23 | 0.5 | 5.037 | Cum
| RB2 | 1 | 14.6 | 0.23 | 0.425 | 1.4271 | Cum
Vertical Beams
| RB3 | 5 | 10 | 0.23 | 0.5 | 5.75 | Cum
[5 empty] | Total | 13 | Cum
| Roof Beams |  | Ground Floor |  | TOTAL | 13 | Cum
e) | Roof Slab
GROUND FLOOR
| Slab-1 | 1 | 11.6 | 10 | 0.125 | 14.5 | Cum
[6 empty] | 16 | Cum
f) | STAIRCASE CONCRETING
Ground Floor
Staircase-1
| Waist slab First Flight | 1 | 4.5 | 1.5 | 0.175 | 1.1812 | Cum
| Steps | 12 | 1.2 | 0.3 | 0.15 | 0.648 | Cum
| Midlanding | 1 | 3 | 1.5 | 0.175 | 0.7875 | Cum
| Mid Landing Beam | 1 | 3 | 0.23 | 0.475 | 0.32775 | Cum
| Waist slab Second Flight | 1 | 4.5 | 1.5 | 0.175 | 1.1812 | Cum
| Steps | 12 | 1.2 | 0.3 | 0.15 | 0.648 | Cum
[6 empty] | 5 | Cum
| Staircase |  | Ground Floor |  | TOTAL | 5 | Cum
g) | Lintels
|  | 2 | 10 | 0.23 | 0.3 | 1.38 | Cum
|  | 3 | 14.6 | 0.23 | 0.3 | 3.0222 | Cum
| Lintels |  | Ground Floor |  | TOTAL | 5 | Cum
h) | CHAJJA's
|  | 1 | 51.6 | 0.6 | 0.075 | 2.322 | Cum
[6 empty] | 3 | Cum
| Chajja's |  | Ground Floor |  | TOTAL | 3 | Cum
RCC Concrete Work
| Total Rcc Qty. All Works Upto Plinth Level. |  |  |  |  | 38 | Cum
| Total Rcc Qty. All Works Above Plinth upto Floor V Level |  |  |  |  | 36 | Cum
| Stair case |  |  |  |  | 5 | Cum
| Chajja's&Lintel |  |  |  |  | 8 | Cum
|  |  |  | Grand Total |  | 87 | Cum
10 | Supplying & Fabrication of Reinforcement steel
| Footings- 60 kg/cum |  | 24 | X | 60 | 1440 | kg
| Plinth Beam- 150 kg/cum |  | 7 | X | 150 | 1050 | kg
| Columns-250 kgs/cum |  | 14 | X | 250 | 3500 | kg
| Roof beams-250 kgs/cum |  | 13 | X | 250 | 3250 | kg
| Slabs-80 kgs/cum |  | 16 | X | 80 | 1280 | kg
| Stair case-100 kgs/cum |  | 5 | X | 100 | 500 | kg
| Lintels etc., -80 kg/cum |  | 5 | X | 80 | 400 | kg
| Chajjas etc., -60 kg/cum |  | 3 | X | 60 | 180 | kg
|  |  | 87 |  |  | 11600 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 580 | kg
[6 empty] | 12180 | KG
[5 empty] | (or) | 13 | MT
11 | SHUTTERING
Under Footing
| F-1 | 15 | 7.2 |  | 0.45 | 48.6 | Sqm
| Total Foundation Shuttering |  |  |  |  | 53 | Sqm
RCC Columns
Below FFL
| C1 | 15 | 1.36 |  | 4.07 | 83.028 | Sqm
[6 empty] | 91 | Sqm
RCC for columns(above FFL upto GF)
| C1 | 15 | 1.36 |  | 4.2 | 85.68 | Sqm
[6 empty] | 94 | Sqm
| Columns Shuttering |  | RCC (upto FFL) |  |  | 91 | Sqm
| Columns Shuttering | Ground Floor (Above FFL) |  |  |  | 94 | Sqm
|  |  |  | Grand Total |  | 185 | Sqm
Shuttering For Plinth Beam
Horizontal Beams
| PB1 | 3 | 14.66 |  | 0.76 | 33.4248 | Sqm
Vertical Beams
| PB2 | 3 | 10.06 |  | 0.76 | 22.9368 | Sqm
[6 empty] | 62 | Sqm
Shuttering For Roof Beams
Ground Floor
Horizontal Beams
| RB1 | 3 | 14.6 |  | 1.23 | 53.874 | Sqm
| RB2 | 1 | 14.6 |  | 1.08 | 15.768 | Sqm
Vertical Beams
| RB3 | 5 | 10 |  | 1.23 | 61.5 | Sqm
[6 empty] | 144 | Sqm
| Roof Beams Shuttering |  | Ground Floor |  |  | 144 | Sqm
Shuttering For Roof Slab
GROUND FLOOR
| Slab-1 | 1 | 11.6 | 10 |  | 116 | Sqm
|  | 1 | 49.2 |  | 0.125 | 6.15 | Sqm
[6 empty] | 134 | Sqm
| Shuttering for Slabs |  | Ground Floor |  |  | 134 | Sqm
Shuttering for Lintels
| 0 | 2 | 10 |  | 0.83 | 16.6 | Sqm
| Sides | 3 | 14.6 |  | 0.83 | 36.354 | Sqm
[5 empty] | Total | 58 | Sqm
Shuttering for Chajjas
| Bottom | 1 | 51.6 | 0.6 |  | 30.96 | Sqm
| Sides | 1 | 54 |  | 0.075 | 4.05 | Sqm
[5 empty] | Total | 39 | Sqm
Shuttering For Stair Case
All Round Length
| Waist slab First Flight | 1 | 4.5 | 1.85 |  | 8.325 | Sqm
| Steps | 12 | 1.5 |  | 0.15 | 2.7 | Sqm
| Midlanding | 1 | 3 | 1.5 |  | 4.5 | Sqm
|  | 1 | 1.5 |  | 0.175 | 0.2625 | Sqm
| Mid Landing Beam | 1 | 3 | 1.13 |  | 3.39 | Sqm
| Waist slab First Flight | 1 | 4.5 | 1.85 |  | 8.325 | Sqm
| Steps | 12 | 1.5 |  | 0.15 | 2.7 | Sqm
[6 empty] | 32 | Sqm
| Staircase |  |  |  |  | 32 | Sqm
12 | Brick Work
CC-Block Masonry Work
Ground Floor
| Horizontal | 3 | 14.6 | 0.2 | 3.2 | 28.032 | Cum
| Vertical | 3 | 10 | 0.2 | 3.2 | 19.2 | Cum
STEPS
| Entrance Steps | 3 | 2.1 | 0.9 | 0.15 | 0.8505 | Cum
|  | 3 | 2.1 | 0.6 | 0.3 | 1.134 | Cum
|  | 3 | 2.1 | 0.3 | 0.45 | 0.8505 | Cum
Deduction
| D1 | 3 | 1.05 | 0.2 | 2.1 | -1.323 | Cum
| W2 | 14 | 1.2 | 0.2 | 1.2 | -4.032 | Cum
| Total 200mm brick work quantity |  |  |  |  | 49 | Cum
| 200mm Thick Brick Work |  | Ground Floor |  | TOTAL | 49 | Cum
13 | 100mm Brick Wall
Half brick masonry
Ground Floor
| Parapet Wall | 1 | 49.2 |  | 0.9 | 44.28 | Sqm
| Total 100 mm brick work quantity |  |  |  |  | 49 | Sqm
| 100 mm Brick Work |  | Ground Floor |  | TOTAL | 49 | Sqm
14 | Plastering
External plastering(18mm)
Ground Floor
| All round | 1 | 49.2 |  | 4.6 | 226.32 | Sqm
| Parapet Wall Plastering | 1 | 49.2 |  | 1.915 | 94.218 | Sqm
Entrance Steps -1
| Sides | 3 | 0.9 |  | 0.45 | 1.215 | Sqm
Deductions of 50% External
| D1 | 1.5 | 1.05 |  | 2.1 | -3.3075 | Sqm
| W5 | 7 | 1.2 |  | 1.2 | -10.08 | Sqm
[5 empty] | Total | 339 | Sqm
| External plastering |  | Ground Floor |  |  | 339 | Sqm
15 | Internal plastering(15mm)
Ground Floor
| Workers Change Room | 1 | 33.2 |  | 3.6 | 119.52 | Sqm
| Workers Rest Room | 1 | 30.4 |  | 3.6 | 109.44 | Sqm
| Stair case room | 1 | 23 |  | 3.6 | 82.8 | Sqm
| Steps | 12 | 1.5 |  | 0.15 | 2.7 | Sqm
|  | 12 | 1.5 |  | 0.3 | 5.4 | Sqm
| Midlanding | 1 | 3 | 1.5 |  | 4.5 | Sqm
|  | 1 | 1.5 |  | 0.175 | 0.2625 | Sqm
| Mid Landing Beam | 1 | 3 | 1.13 |  | 3.39 | Sqm
| Steps | 12 | 1.5 |  | 0.15 | 2.7 | Sqm
|  | 12 | 1.5 |  | 0.3 | 5.4 | Sqm
Deductions of 50% Internal
| D1 | 1.5 | 1.05 |  | 2.1 | -3.3075 | Sqm
| W5 | 7 | 1.2 |  | 1.2 | -10.08 | Sqm
[5 empty] | Total | 355 | Sqm
| Internal plastering |  | Ground Floor |  | TOTAL | 355 | Sqm
16 | Ceiling plastering
GROUND FLOOR
| Workers Change Room | 1 | 11.2 | 5.4 |  | 60.48 | Sqm
| Workers Rest Room | 1 | 11.2 | 4 |  | 44.8 | Sqm
| Open Beams | 2 | 13.91 |  | 1 | 27.82 | Sqm
| Vertical open Beams | 2 | 9.77 |  | 1 | 19.54 | Sqm
| Waist slab First Flight | 1 | 4.5 | 1.675 |  | 7.5375 | Sqm
| Waist slab First Flight | 1 | 4.5 | 1.675 |  | 7.5375 | Sqm
Chajja's Plastering
|  | 2 | 51.6 | 0.6 |  | 61.92 | Sqm
|  | 1 | 54 |  | 0.075 | 4.05 | Sqm
[6 empty] | 257 | Sqm
| Ceiling plastering |  | Ground Floor |  | TOTAL | 257 | Sqm
17 | Pointing on stone work
Above NGL
| All Round Length | 1 | 0 |  | 0 | 0 | Sqm
[6 empty] | 0 | Sqm
| Pointing Work |  |  |  | TOTAL | 0 | Sqm
18 | Plaster drip course/water patti
| Sunshade | 1 | 54 |  |  | 54 | Rmt
| Parapet Wall Watter Patti | 1 | 49.2 |  |  | 49.2 | Rmt
[5 empty] | Total | 114 | Rmt
19 | Flooring
Granolithick Flooring
Ground Floor
| Workers Change Room | 1 | 14.2 | 5.4 |  | 76.68 | Sqm
| Workers Rest Room | 1 | 14.2 | 4 |  | 56.8 | Sqm
[5 empty] | Total | 147 | Sqm
| Granolithick Flooring |  | Ground Floor |  | TOTAL | 147 | Sqm
20 | Skirting
| Workers Change Room | 1 | 39.2 |  | 0.1 | 3.92 | Sqm
| Workers Rest Room | 1 | 36.4 |  | 0.1 | 3.64 | Sqm
| CC Flooring Skirting |  |  |  | Total | 8 | Sqm
21 | Kota Stone Flooring
Ground Floor
For Stair Case Area
Entrance Steps - 1,2&3
| Threads | 9 | 2 | 0.3 |  | 5.4 | Sqm
| Raiser | 9 | 2 |  | 0.15 | 2.7 | Sqm
[5 empty] | Total | 9 | Sqm
| Kota Stone Flooring |  | Ground Floor |  | TOTAL | 9 | Sqm
22 | 18mm thick gang saw cut mirror polished
Doors & Window Sills
| D1 | 3 | 1.05 | 0.2 |  | 0.63 | Sqm
| W5 | 14 | 1.2 | 0.2 |  | 3.36 | Sqm
[5 empty] | Total | 4 | Sqm
|  |  |  | Grand Total |  | 4 | Sqm
23 | Painting
| External painting |  |  |  |  | 339 | Sqm
| Internal painting |  |  |  |  | 612 | Sqm
| Internal&External Paint With White Cement Based Putty |  |  | Ground Floor |  | 951 | Sqm
| Ceiling painting - White wash |  |  |  |  | 0 | Sqm
24 | Water Proofing works
Ground Floor
Terrace Water Proofing
| Terrace | 1 | 14.6 | 10 |  | 146 | Sqm
[5 empty] | Total | 161 | Sqm
25 | Joinery
Ground Floor
WPC Door Shutter 35mm Thick
| D1 | 3 | 1.05 |  | 2.1 | 6.615 | Sqm
[6 empty] | 7 | Sqm
| shutters |  |  |  | Total | 7 | Sqm
b) WPC Door Frame
Ground Floor
| D1 | 3 | 5.25 |  |  | 15.75 | Rmt
[6 empty] | 16 | Rmt
| WPC Door Frames |  |  |  | TOTAL | 16 | Rmt
26 | UPVC Sliding Window
Ground Floor
UPVC WINDOWS
| W2 | 14 | 1.2 |  | 1.2 | 20.16 | Sqm
[5 empty] | Total | 20 | Sqm
| UPVC Sliding Window |  |  |  | Total | 20 | Sqm
27 | Ventilators Louvers
| V1 | 14 | 1.2 |  | 0.6 | 10.08 | Sqm
[6 empty] | 10 | Sqm
| Ventilators |  |  |  | Total | 10 | Sqm
28 | Hydraulic Door Closer
| D1 | 6 |  |  |  | 6 | No's
[6 empty] | 6 | No's
29 | MS Grills For Windows
| MS Grills 20kg/Sqm | 0 | 0 |  |  | 0 | KGS
| Convertion (20kg/Sqm) |  |  |  |  | 0 | KGS
30 | Synthatic Enamel Paint
a) Steel surfaces with zinc chromate primer
Windows For MS Grill
| W2 | 0 | 0 |  | 0 | 0 | Sqm
[5 empty] | Total | 0 | Sqm
b) Wooden surface with approved primer
| D1 | 3 | 1.05 |  | 2.1 | 6.615 | Sqm
[5 empty] | Total | 7 | Sqm
|  |  |  | Grand Total |  | 7 | Sqm
31 | Rain water down take pipes
| 110mm Dia | 8 | 5.4 |  |  | 43.2 | Rmt
[5 empty] | Total | 44 | Rmt
32 | 150mmØ SWR SOIL WASTE PIPE | 1 | 25 |  |  | 25 | Rmt
[6 empty] | 25 | Rmt
33 | S.W. gully trap
|  | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
34 | Gully chamber
|  | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
35 | Inspection Chamber
| IC 450 x 600 mm | 1 | 6 |  |  | 6
| Total Qty |  |  |  |  | 6 | Nos
36 | Manhole
| 500mm Dia Top and 1200mm Dia Bottom | 1 | 4 |  |  | 4
| Total Qty |  |  |  |  | 4 | Nos
37 | 50mmØ SWR /PVC WASTE Water PIPE | 1 | 2 |  |  | 2 | Rmt
[6 empty] | 2 | Rmt
38 | WASH BASINS
| Toilet Block | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
39 | Bottle Trap
| Toilet Block | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
40 | Floor Trap
| Toilet Block | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
41 | Mirror Glass
| Toilet Block | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
42 | Angle Valve
| Toilet Block | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
43 | 25mmØ CPVC Line | 1 | 35 |  |  | 35 | Rmt
[6 empty] | 35 | Rmt
44 | Gate Valve
| 25mm dia | 1 | 1 |  |  | 1
[6 empty] | 1 | Nos
45 | Syntex Tank
| 1500 Liter Capacity | 1 | 1 |  |  | 1
[6 empty] | 1 | Nos

## Health Care Center DTL
PROPOSED CONSTRUCTION OF HEALTH CARE CENTER , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Health Care Center
1 | Site levelling | 1 | 20.23 | 12.75 |  | 257.9325 | Sqm
[5 empty] | Total | 258 | Sqm
2 | Earth Work excavation
Under Footing For Stair Case
A) Upto 1.50 M
| F1 | 12 | 2.1 | 2.1 | 1.5 | 79.38 | Cum
| F2 | 2 | 2.4 | 2.4 | 1.5 | 17.28 | Cum
Under RR Masonry
| ALL Round Length | 1 | 45.96 | 0.53 | 0.7 | 14.7213 | Cum
| For Ramp | 1 | 9 | 1.5 | 0.7 | 5.775 | Cum
| Total |  |  |  |  | 123 | Cum
Above 1.50 till 3.00 M
| F1 | 12 | 2.1 | 2.1 | 1.5 | 79.38 | Cum
| F2 | 2 | 2.4 | 2.4 | 1.5 | 17.28 | Cum
| Total |  |  |  |  | 101 | Cum
Above 3.00 till 4.50 M
| F1 | 12 | 2.1 | 2.1 | 1.5 | 79.38 | Cum
| F2 | 2 | 2.4 | 2.4 | 1.5 | 17.28 | Cum
| Total |  |  |  |  | 101 | Cum
| Total Quantity of Excavation |  |  |  |  | 325 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 325 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | -24 | Cum
| Sand Cohesion |  |  |  |  | -31 | Cum
| RCC Footing |  |  |  |  | -23 | Cum
| Below FFL Column |  |  |  |  | -7 | Cum
| Plinth Beam |  |  |  |  | -8 | Cum
| Below FFL RR Masonry |  |  |  |  | -30 | Cum
| Back fillingQty |  |  |  |  | 202 | Cum
| Basement Filling | 1 | 15 | 7.75 | 1 | 116.25 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | -7 | Cum
| Filling With Available Excavated Earth Considered |  |  |  |  | 325 | Cum
| Disposal of Excavated Earth |  |  |  |  | 0 | Cum
4 | PCC (1:4:8)
Under Footing
| F1 | 12 | 2.1 | 2.1 | 0.1 | 5.292 | Cum
| F2 | 2 | 2.4 | 2.4 | 0.1 | 1.152 | Cum
[5 empty] | Total | 6.7662 | Cum
Under RR Masonry
|  | 1 | 45.96 | 0.53 | 0.1 | 2.4359 | Cum
|  | 1 | 9 | 1.5 | 0.1 | 1.35 | Cum
[5 empty] | Total | 3.9752 | Cum
Under Room PCC
| Health Care Center | 1 | 16 | 8 | 0.1 | 12.8 | Cum
| Total |  |  |  | Total | 13.44 | Cum
| Total PCC quantity |  |  |  |  | 24 | Cum
5 | 230mm Thick Soling
Under Room
| Health Care Center | 1 | 15 | 7.75 | 0.23 | 26.7375 | Cum
| For Ramp | 1 | 9 | 1.35 | 0.23 | 2.7945 | Cum
[5 empty] | Total | 31 | Cum
6 | ATT
| Anti terminate | 1 | 15 | 7.75 |  | 116 | Sqm
[6 empty] | 122 | Sqm
| TOTAL ATT Qty. |  |  |  |  | 122 | Sqm
7 | RR MASONRY
Under RR Masonry
Below NGL
| All Round Length | 1 | 45.96 | 0.38 | 0.6 | 10.4789 | Cum
| For Ramp Side Wall | 1 | 11 | 0.38 | 0.6 | 2.508 | Cum
[6 empty] | 14 | Cum
Above NGL
| All Round Length | 1 | 45.96 | 0.38 | 0.62 | 10.8282 | Cum
| For Stair Case | 1 | 13.75 | 0.38 | 0.45 | 2.3512 | Cum
| For Ramp Side Wall | 1 | 11 | 0.38 | 0.6 | 2.508 | Cum
[6 empty] | 16 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 30 | Cum
8 | Plinth Protection
|  | 1 | 45 | 0.75 |  | 34 | Sqm
[6 empty] | 36 | Sqm
| Total Plinth Protection Qty. |  |  |  |  | 36 | Sqm
9 | R.C.C
a) | Under Footing
| F1 | 12 | 1.8 | 1.8 | 0.45 | 17.496 | Cum
| F2 | 2 | 2.1 | 2.1 | 0.5 | 4.41 | Cum
| Total footings RCC |  |  |  |  | 23 | Cum
b) | RCC Columns
GROUND FLOOR
Below FFL
| C1 | 14 | 0.23 | 0.45 | 4.57 | 6.6219 | Cum
| Total columns RCC (upto FFL) |  |  |  |  | 7 | Cum
RCC for columns(above FFL upto GF)
| C1 | 14 | 0.23 | 0.45 | 3.2 | 4.6368 | Cum
First Floor
| C1 | 14 | 0.23 | 0.45 | 3.2 | 4.6368 | Cum
| Total |  |  |  |  | 10 | Cum
| Columns |  | RCC (upto FFL) |  |  | 7 | Cum
| Columns |  | G+1 Floor |  |  | 10 | Cum
[5 empty] | TOTAL | 17 | Cum
c) | Plinth Beam
Horizontal Beams
| PB1 | 3 | 15.23 | 0.23 | 0.38 | 3.9933 | Cum
Vertical Beams
| PB2 | 5 | 7.78 | 0.23 | 0.38 | 3.3999 | Cum
| Total |  |  |  |  | 8 | Cum
d) | RCC FOR ROOF BEAMS
Ground Floor
Horizontal Beams
|  | 3 | 15.23 | 0.23 | 0.375 | 3.9408 | Cum
|  | 5 | 7.75 | 0.23 | 0.45 | 4.0106 | Cum
|  | 1 | 4.2 | 0.23 | 0.45 | 0.4347 | Cum
First Floor
|  | 3 | 15.23 | 0.23 | 0.375 | 3.9408 | Cum
|  | 5 | 7.75 | 0.23 | 0.45 | 4.0106 | Cum
|  | 1 | 4.2 | 0.23 | 0.45 | 0.4347
[5 empty] | Total | 18 | Cum
| Roof Beams |  | G+1 Floor |  |  | 18 | Cum
e) | Roof Slab
GROUND FLOOR
| Slab-1 | 1 | 12.23 | 7.75 | 0.125 | 11.8478 | Cum
First Floor
| Slab-1 | 1 | 15.23 | 7.75 | 0.125 | 14.7541 | Cum
[6 empty] | 28 | Cum
| Roof Slab |  | G+1 Floor |  |  | 28 | Cum
f) | STAIRCASE CONCRETING
Ground Floor
Staircase-1
| Waist slab First Flight | 1 | 4.5 | 1.5 | 0.175 | 1.1812 | Cum
| Steps | 12 | 1.5 | 0.3 | 0.15 | 0.81 | Cum
| Midlanding | 1 | 3 | 1.5 | 0.175 | 0.7875 | Cum
| Mid Landing Beam | 1 | 3 | 0.23 | 0.475 | 0.32775 | Cum
| Waist slab Second Flight | 1 | 4.5 | 1.5 | 0.175 | 1.1812 | Cum
| Steps | 12 | 1.5 | 0.3 | 0.15 | 0.81
[6 empty] | 5 | Cum
| Staircase |  | Ground Floor |  | TOTAL | 5 | Cum
|  |  |  | Grand Total |  | 5 | Cum
g) | Lintels
GROUND FLOOR
|  | 2 | 15.23 | 0.2 | 0.45 | 2.7414 | Cum
|  | 3 | 7.75 | 0.2 | 0.45 | 2.0925 | Cum
|  | 1 | 12 | 0.2 | 0.45 | 1.08 | Cum
|  | 3 | 3.5 | 0.1 | 0.25 | 0.2625 | Cum
|  | 2 | 3 | 0.1 | 0.25 | 0.15 | Cum
|  | 1 | 6.1 | 0.1 | 0.25 | 0.1525 | Cum
| Lintels |  | G+1 Floor |  | TOTAL | 7 | Cum
h) | CHAJJA's
GROUND FLOOR
|  | 2 | 16.43 | 0.6 | 0.075 | 1.4787 | Cum
|  | 2 | 7.75 | 0.6 | 0.075 | 0.6975 | Cum
[6 empty] | 2 | Cum
| Chajja's |  | G+1 Floor |  | TOTAL | 2 | Cum
RCC Concrete Work
| Total Rcc Qty. All Works Upto Plinth Level. |  |  |  |  | 38 | Cum
| Total Rcc Qty. All Works Above Plinth upto Floor V Level |  |  |  |  | 61 | Cum
| Chajja's&Lintel |  |  |  |  | 9 | Cum
|  |  |  | Grand Total |  | 108 | Cum
10 | Supplying & Fabrication of Reinforcement steel
| Footings- 60 kg/cum |  | 23 | X | 60 | 1380 | kg
| Plinth Beam- 150 kg/cum |  | 8 | X | 150 | 1200 | kg
| Columns-250 kgs/cum |  | 17 | X | 250 | 4250 | kg
| Roof beams-250 kgs/cum |  | 18 | X | 250 | 4500 | kg
| Slabs-80 kgs/cum |  | 28 | X | 80 | 2240 | kg
| Stair case-100 kgs/cum |  | 5 | X | 100 | 500 | kg
| Lintels etc., -80 kg/cum |  | 7 | X | 80 | 560 | kg
| Chajjas etc., -60 kg/cum |  | 2 | X | 60 | 120 | kg
|  |  | 108 |  |  | 14750 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 738 | kg
[6 empty] | 15488 | KG
[5 empty] | (or) | 16 | MT
11 | SHUTTERING
Under Footing
| F1 | 12 | 7.2 |  | 0.45 | 38.88 | Sqm
| F2 | 2 | 8.4 |  | 0.5 | 8.4 | Sqm
| Total Foundation Shuttering |  |  |  |  | 50 | Sqm
RCC Columns
Below FFL
| C1 | 14 | 1.36 |  | 4.57 | 87.0128 | Sqm
[6 empty] | 91 | Sqm
RCC for columns(above FFL upto GF)
| C1 | 14 | 1.36 |  | 3.2 | 60.928 | Sqm
First Floor
| C1 | 14 | 1.36 |  | 3.2 | 60.928 | Sqm
[6 empty] | 134 | Sqm
| Columns Shuttering |  | RCC (upto FFL) |  |  | 91 | Sqm
| Columns Shuttering | Ground Floor For Stiar Case (Above FFL) |  |  |  | 134 | Sqm
|  |  |  | Grand Total |  | 225 | Sqm
Shuttering For Plinth Beam
Horizontal Beams
| PB1 | 3 | 15.23 |  | 0.76 | 34.7244 | Sqm
Vertical Beams
| PB2 | 5 | 7.78 |  | 0.76 | 29.564 | Sqm
[6 empty] | 68 | Sqm
Shuttering For Roof Beams
Ground Floor
|  | 3 | 15.23 |  | 0.73 | 33.3537 | Sqm
|  | 5 | 7.75 |  | 0.88 | 34.1 | Sqm
|  | 1 | 4.2 |  | 0.88 | 3.696 | Sqm
First Floor
|  | 3 | 15.23 |  | 0.73 | 33.3537 | Sqm
|  | 5 | 7.75 |  | 0.88 | 34.1 | Sqm
|  | 1 | 4.2 |  | 0.88 | 3.696 | Sqm
[6 empty] | 149 | Sqm
| Roof Beams Shuttering |  | G+1 Floor |  |  | 149 | Sqm
Shuttering For Roof Slab
GROUND FLOOR
| Slab-1 | 1 | 12.23 | 7.75 |  | 94.7825 | Sqm
First Floor
| Slab-1 | 1 | 15.23 | 7.75 |  | 118.0325 | Sqm
[6 empty] | 223 | Sqm
| Shuttering for Slabs |  | G+1 Floor |  |  | 223 | Sqm
Shuttering For Stair Case
Ground Floor
Staircase-1
| Waist slab First Flight | 1 | 4.5 | 1.85 |  | 8.325 | Sqm
| Steps | 12 | 1.5 |  | 0.15 | 2.7 | Sqm
| Midlanding | 1 | 3 | 1.5 |  | 4.5 | Sqm
|  | 1 | 1.5 |  | 0.175 | 0.2625 | Sqm
| Mid Landing Beam | 1 | 3 | 1.13 |  | 3.39 | Sqm
| Waist slab First Flight | 1 | 4.5 | 1.85 |  | 8.325 | Sqm
| Steps | 12 | 1.5 |  | 0.15 | 2.7 | Sqm
[6 empty] | 32 | Sqm
| Staircase |  |  |  |  | 32 | Sqm
|  |  |  | Grand Total |  | 32 | Sqm
Shuttering for Lintels
Ground Floor
|  | 2 | 15.23 |  | 1.1 | 33.506 | Sqm
|  | 3 | 7.75 |  | 1.1 | 25.575 | Sqm
|  | 1 | 12 |  | 1.1 | 13.2 | Sqm
|  | 3 | 3.5 |  | 0.6 | 6.3 | Sqm
|  | 2 | 3 |  | 0.6 | 3.6 | Sqm
|  | 1 | 6.1 |  | 0.6 | 3.66 | Sqm
|  |  | G+1 Floor |  | Total | 90 | Sqm
Shuttering for Chajjas
Ground Floor
|  | 2 | 16.43 | 0.675 |  | 22.1805 | Sqm
|  | 2 | 7.75 | 0.675 |  | 10.4625 | Sqm
|  |  | G+1 Floor |  | Total | 34 | Sqm
12 | Brick Work
CC-Block Masonry Work
Ground Floor
| Horizontal | 3 | 15 | 0.2 | 3 | 27 | Cum
| Vertical | 3 | 7.75 | 0.2 | 3 | 13.95 | Cum
STEPS
| Entrance Steps | 2 | 2.1 | 0.9 | 0.15 | 0.567 | Cum
|  | 2 | 2.1 | 0.6 | 0.3 | 0.756 | Cum
|  | 2 | 2.1 | 0.3 | 0.45 | 0.567 | Cum
Deduction
| D1 | 2 | 1.2 | 0.2 | 2.1 | -1.008 | Cum
| D2 | 4 | 0.9 | 0.2 | 2.1 | -1.512 | Cum
| W1 | 6 | 1.5 | 0.2 | 1.2 | -2.16 | Cum
| W2 | 4 | 1.2 | 0.2 | 1.2 | -1.152 | Cum
| V1 | 1 | 0.9 | 0.2 | 0.6 | -0.108 | Cum
First Floor
| Vertical | 3 | 7.75 | 0.2 | 1 | 4.65 | Cum
| Total 200 mm brick work quantity |  |  |  |  | 44 | Cum
| 200mm Thick Brick Work |  | G+1 Floor |  | TOTAL | 44 | Cum
13 | 100mm Brick Wall
Half brick masonry
Ground Floor
| Toilet | 1 | 5.3 |  | 3.5 | 18.55 | Sqm
| Store Room | 1 | 3 |  | 3.5 | 10.5 | Sqm
| Compounder Room | 1 | 6.585 |  | 3.5 | 23.0475 | Sqm
| Dressing Room | 1 | 5.05 |  | 3.5 | 17.675 | Sqm
| Parapet Wall | 2 | 45.56 |  | 0.9 | 82.008 | Sqm
| Staircase | 2 | 4.5 |  | 0.9 | 8.1 | Sqm
Deduction
| W1 | 1 | 1.5 |  | 1.2 | -1.8 | Sqm
| D2 | 2 | 0.9 |  | 2.1 | -3.78 | Sqm
| D3 | 1 | 0.75 |  | 2.1 | -1.575 | Sqm
| Total 100 mm brick work quantity |  |  |  |  | 161 | Sqm
| 100 mm Brick Work |  | G+1 Floor |  |  | 161 | Sqm
14 | Plastering
External plastering(18mm)
Ground Floor
| All round | 1 | 46.5 |  | 4.6 | 213.9 | Sqm
Entrance Steps -1
| Sides | 2 | 0.9 |  | 0.45 | 0.81 | Sqm
Deductions of 50% External
| D1 | 1 | 1.05 |  | 2.1 | -2.205 | Sqm
| D2 | 0.5 | 0.9 |  | 2.1 | -0.945 | Sqm
| W1 | 3 | 1.5 |  | 1.2 | -5.4 | Sqm
| W2 | 2 | 1.2 |  | 1.2 | -2.88 | Sqm
| V1 | 0.5 | 0.9 |  | 0.6 | -0.27 | Sqm
First Floor
| Parapet Wall Plastering | 1 | 46.5 |  | 2.2 | 102.3 | Sqm
Terrace
| Parapet Wall Plastering | 1 | 46.7 |  | 2.45 | 114.415 | Sqm
[5 empty] | Total | 441 | Sqm
| External plastering |  | G+1 Floor |  |  | 441 | Sqm
15 | Internal plastering(15mm)
Ground Floor
| Doctor room | 1 | 13.38 |  | 3.5 | 46.83 | Sqm
| Toilet | 1 | 6.8 |  | 3.5 | 23.8 | Sqm
| Rest Room | 1 | 11.48 |  | 3.5 | 40.18 | Sqm
| Toilet Front | 1 | 3.36 |  | 3.5 | 11.76 | Sqm
| Store Room | 1 | 12.62 |  | 3.5 | 44.17 | Sqm
| Passage | 1 | 13.4 |  | 3.5 | 46.9 | Sqm
| Waiting Hall | 1 | 20.6 |  | 3.5 | 72.1 | Sqm
| Compounder Room | 1 | 12.93 |  | 3.5 | 45.255 | Sqm
| Dressing Room | 1 | 9.86 |  | 3.5 | 34.51 | Sqm
| Staircase room | 2 | 7.75 |  | 3.5 | 54.25 | Sqm
|  | 2 | 3 |  | 3.5 | 21 | Sqm
|  | 2 | 4.5 |  | 2 | 18 | Sqm
Deductions of 50% Internal
| D1 | 1 | 1.2 |  | 2.1 | -2.52 | Sqm
| D2 | 3 | 0.9 |  | 2.1 | -5.67 | Sqm
| D3 | 0.5 | 0.75 |  | 2.1 | -0.7875 | Sqm
| W1 | 3.5 | 1.5 |  | 1.2 | -6.3 | Sqm
| W2 | 2 | 1.2 |  | 1.2 | -2.88 | Sqm
| V1 | 0.5 | 0.9 |  | 0.6 | -0.27 | Sqm
[5 empty] | Total | 462 | Sqm
| Internal plastering |  | G+1 Floor |  | TOTAL | 462 | Sqm
16 | Ceiling plastering
GROUND FLOOR
| Doctor room | 1 | 3.69 | 3 |  | 11.07 | Sqm
| Toilet | 1 | 1.5 | 1.9 |  | 2.85 | Sqm
| Rest Room | 1 | 2.74 | 3 |  | 8.22 | Sqm
| Toilet Front | 1 | 1 | 1.74 |  | 1.74 | Sqm
| Store Room | 1 | 3.31 | 3 |  | 9.93 | Sqm
| Passage | 1 | 6.1 | 1.2 |  | 7.32 | Sqm
| Waiting Hall | 1 | 5.9 | 4.4 |  | 25.96 | Sqm
| Compounder Room | 1 | 3.635 | 2.83 |  | 10.287 | Sqm
| Dressing Room | 1 | 2.1 | 2.83 |  | 5.943 | Sqm
| Open Beams | 1 | 6.2 |  | 0.9 | 5.58 | Sqm
| stair case | 1 | 2.4 | 7.75 |  | 18.6 | Sqm
| Waist slab | 2 | 4.5 | 1.5 |  | 13.5 | Sqm
| Mid landing | 1 | 3 | 1.5 |  | 4.5 | Sqm
Chajja's Plastering
|  | 4 | 16.43 | 0.6 |  | 39.432 | Sqm
|  | 4 | 7.75 | 0.6 |  | 18.6 | Sqm
First Floor
|  | 1 | 15.23 | 7.75 |  | 118.0325 | Sqm
|  | 3 | 15.23 |  | 0.73 | 33.3537 | Sqm
|  | 5 | 7.75 |  | 0.88 | 34.1 | Sqm
|  | 1 | 4.2 |  | 0.88 | 3.696 | Sqm
[6 empty] | 391 | Sqm
| Ceiling plastering |  | G+1 Floor |  | TOTAL | 391 | Sqm
17 | Pointing on stone work
Above NGL
| All Round Length | 1 | 45.96 |  | 0.62 | 28.4952 | Sqm
| For Stair Case | 1 | 13.75 |  | 0.45 | 6.1875 | Sqm
| For Ramp Side Wall | 1 | 11 |  | 0.6 | 6.6 | Sqm
[6 empty] | 43 | Sqm
| Pointing Work |  |  |  | TOTAL | 43 | Sqm
18 | Plaster drip course/water patti
Ground Floor
|  | 1 | 50.76 |  |  | 50.76 | Rmt
| Parapet Wall Watter Patti | 1 | 39.56 |  |  | 39.56 | Rmt
[5 empty] | Total | 95 | Rmt
False ceiling
19 | Mineral fiber false ceiling
| Doctor room | 1 | 3.69 | 3 |  | 11.07 | Sqm
[6 empty] | 12 | Sqm
FLOORING
20 | C.C. flooring and platforms of mix M-25
VDF Flooring HCC Building Out Side 3m Wide Area
| Staircase | 1 | 7.75 | 3 | 0.125 | 2.9062 | Cum
| For Ramp Area | 1 | 6.6 | 1.8 | 0.125 | 1.485 | Cum
| Aproach road | 1 | 5 | 2 | 0.125 | 1.25 | Cum
[5 empty] | Total | 6 | Cum
| VDF Flooring |  |  |  | TOTAL | 6 | Cum
21 | Cutting Grooves and filling with silicon waterproof sealant
| for every 3 m x 4m size area | 0.5 | 14 | - | - | 7 | RM
[5 empty] | Say | 7 | RM
22 | Laying of Hot top
| Staircase | 1 | 7.75 | 3 |  | 23.25 | Sqm
| For Ramp Area | 1 | 6.6 | 1.8 |  | 11.88 | Sqm
| Aproach road | 1 | 5 | 2 |  | 10 | Sqm
[6 empty] | 50 | Sqm
23 | Vitrified Flooring Tiles
Ground Floor
| Doctor Room | 1 | 3.69 | 3 |  | 11.07 | Sqm
| Rest Room | 1 | 2.74 | 3 |  | 8.22 | Sqm
| Toilet Front Area\ | 1 | 1.74 | 1 |  | 1.74 | Sqm
| Store room | 1 | 3.31 | 3 |  | 9.93 | Sqm
| Waiting Hall | 1 | 5.9 | 4.4 |  | 25.96 | Sqm
| Compounder Room | 1 | 3.635 | 2.83 |  | 10.287 | Sqm
| Dressing Room | 1 | 2.1 | 2.83 |  | 5.943 | Sqm
| Passage | 1 | 6.1 | 1.2 |  | 7.32 | Sqm
[5 empty] | Total | 84 | Sqm
| Vitrified Flooring |  | G+1 Floor |  | TOTAL | 84 | Sqm
24 | Skirting
Ground Floor
| Doctor Room | 1 | 13.38 |  | 0.1 | 1.338 | Sqm
| Rest Room | 1 | 11.48 |  | 0.1 | 1.148 | Sqm
| Toilet Front Area\ | 1 | 5.48 |  | 0.1 | 0.548 | Sqm
| Store room | 1 | 12.62 |  | 0.1 | 1.262 | Sqm
| Waiting Hall | 1 | 20.6 |  | 0.1 | 2.06 | Sqm
| Compounder Room | 1 | 12.93 |  | 0.1 | 1.293 | Sqm
| Dressing Room | 1 | 9.86 |  | 0.1 | 0.986 | Sqm
| Passage | 1 | 14.6 |  | 0.1 | 1.46 | Sqm
| Vitrified Flooring Skirting |  | G+1 Floor |  | Total | 11 | Sqm
25 | Granolithic Flooring
Ground Floor
| Store Room |  |  |  |  | 0 | Sqm
| For Ramp & Beside Area |  |  |  |  | 0 | Cum
First Floor
| Store Room |  |  |  |  | 0 | Sqm
| Granolithick Flooring |  |  |  | Total | 0 | Sqm
26 | Skirting
Ground Floor
| Store Room |  |  |  |  | 0 | Sqm
First Floor
| Store Room |  |  |  |  | 0 | Sqm
|  |  | G+1 Floor |  | Total | 0 | Sqm
27 | 18mm thick gang saw cut mirror polished
Ground Floor
Doors & Window Sills
| D1 | 1 | 1.05 | 0.2 |  | 0.21 | Sqm
| D2 | 5 | 0.9 | 0.2 |  | 0.9 | Sqm
| W1 | 7 | 1.5 | 0.2 |  | 2.1 | Sqm
| W2 | 4 | 1.2 | 0.2 |  | 0.96 | Sqm
[5 empty] | Total | 4 | Sqm
|  |  | G+1 Floor |  |  | 4 | Sqm
28 | Kota Stone Flooring
Ground Floor
Entrance Steps - 1
| Threads | 6 | 1.8 | 0.3 |  | 3.24 | Sqm
| Raiser | 6 | 1.8 |  | 0.15 | 1.62 | Sqm
Stair Case
| Thread | 24 | 1.5 | 0.3 |  | 10.8 | Sqm
| Raiser | 24 | 1.5 |  | 0.15 | 5.4 | Sqm
| Landing | 1 | 3 | 1.5 |  | 4.5 | Sqm
| open Space Balcony | 1 | 4.2 | 3 |  | 12.6 | Sqm
[5 empty] | Total | 40 | Sqm
| Kota Stone Flooring |  | G+1 Floor |  | TOTAL | 40 | Sqm
29 | Non Skid Flooring
Ground Floor
| Toilet | 1 | 1.5 | 1.9 |  | 2.85 | Sqm
First Floor
| Toilet | 1 | 1.5 | 1.9 |  | 2.85 | Sqm
[5 empty] | Total | 6 | Sqm
| Non Skid Flooring |  | G+1 Floor |  | TOTAL | 6 | Sqm
30 | Dadoing
Ground Floor
| Toilet | 1 | 6.8 |  | 2.875 | 19.55 | Sqm
First Floor
| Toilet | 1 | 6.8 |  | 2.875 | 19.55 | Sqm
[5 empty] | Total | 41 | Sqm
| Non Skid Flooring |  | G+1 Floor |  | TOTAL | 41 | Sqm
31 | Painting
| External painting |  |  | G+1 Floor |  | 441 | Sqm
| Internal painting |  |  | G+1 Floor |  | 853 | Sqm
| Internal&External Paint With White Cement Based Putty |  |  | G+1 Floor |  | 1294 | Sqm
| Ceiling painting - White wash |  |  | G+1 Floor |  | 0 | Sqm
32 | Water Proofing works
Terrace
Terrace Water Proofing
| Terrace | 1 | 15.5 | 7.75 |  | 120.125 | Sqm
|  | 1 | 12.5 | 7.75 |  | 96.875 | Sqm
[5 empty] | Total | 228 | Sqm
33 | Joinery
Ground Floor
WPC Door Shutter 35mm Thick
| D1 | 1 | 1.2 |  | 2.1 | 2.52 | Sqm
| D2 | 6 | 0.9 |  | 2.1 | 11.34 | Sqm
[6 empty] | 15 | Sqm
| shutters |  | G+1 Floor |  | Total | 15 | Sqm
b) WPC Door Frame
Ground Floor
| D1 | 1 | 5.4 |  |  | 5.4 | Rmt
| D2 | 6 | 5.1 |  |  | 30.6 | Rmt
| WPC Door Frame |  | G+1 Floor |  | TOTAL | 36 | Rmt
34 | WPC Door Shutter 30mm Thick
Ground Floor
| D3 | 1 | 0.75 |  | 2.1 | 1.575 | Sqm
[6 empty] | 2 | Sqm
| shutters |  |  |  | Total | 2 | Sqm
b) WPC Door Frame
Ground Floor
| D3 | 1 | 4.95 |  |  | 4.95 | Rmt
[6 empty] | 5 | Rmt
| WPC Door Frame |  | G+1 Floor |  | TOTAL | 5 | Rmt
34 | UPVC WINDOWS
Ground Floor
UPVC WINDOWS
| W1 | 7 | 1.5 |  | 1.2 | 12.6 | Sqm
| W2 | 4 | 1.2 |  | 1.2 | 5.76 | Sqm
[5 empty] | Total | 19 | Sqm
| UPVC Sliding Window |  | G+1 Floor |  | Total | 19 | Sqm
35 | UPVC Ventilator
Ground Floor
| V1 | 7 | 1.5 |  | 0.6 | 6.3 | Sqm
| V2 | 4 | 1.2 |  | 0.6 | 2.88 | Sqm
| V3 | 1 | 0.9 |  | 0.6 | 0.54 | Sqm
|  |  | G+1 Floor |  | Total | 10 | Sqm
36 | Hydraulic Door Closer
Ground Floor
| D1 | 2 |  |  |  | 2 | No's
| D2 | 6 |  |  |  | 6 | No's
|  |  | G+1 Floor |  |  | 8 | No's
37 | MS Grills For Windows
| MS Grills 20kg/Sqm |  |  |  |  | 0 | KGS
| Convertion (20kg/Sqm) |  | G+1 Floor |  |  | 0 | KGS
38 | S.S Railing
Ground Floor
| Ramp | 1 | 7.8 |  | 0.9 | 7.02 | Sqm
| Steps | 2 | 2 |  | 0.9 | 3.6 | Sqm
[6 empty] | 11 | Sqm
|  |  |  | Grand Total |  | 11 | Sqm
| SS TUBES 25KGS /Sqm | 25 |  |  |  | 275 | KGS
39 | Synthatic Enamel Paint
Ground Floor
a) Steel surfaces with zinc chromate primer
[6 empty] | 0 | Sqm
|  |  | G+1 Floor |  | Total | 0 | Sqm
Ground Floor
b) Wooden surface with approved primer
| D1 | 1 | 1.05 |  | 2.4 | 2.52 | Sqm
| D2 | 6 | 0.9 |  | 2.4 | 12.96 | Sqm
| D3 | 4 | 0.75 |  | 2.4 | 7.2 | Sqm
|  |  | G+1 Floor |  | Total | 24 | Sqm
|  |  |  | Grand Total |  | 24 | Sqm
SEWAGE
40 | Single piece EWC with soft PP
Ground floor
| Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty. |  | G+1 Floor |  |  | 1 | Nos
41 | health faucet
Ground floor
| Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty. |  |  |  |  | 1 | Nos
42 | Urinals
Ground floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
43 | Urinal Partitions
Ground floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
44 | Paper holder
Ground floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
45 | Health Faucet
Ground floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
46 | Gully Trap
| Toilet | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
47 | Gully chamber
| Toilet | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
47 | P or S Trap
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
48 | Inspection Chamber
| IC 450 x 600 mm | 1 | 3 |  |  | 3
| Total Qty |  |  |  |  | 3 | Nos
49 | Manhole
| 500mm Dia Top and 1200mm Dia Bottom | 1 | 6 |  |  | 6
| Total Qty |  |  |  |  | 6 | Nos
50 | Soil Pipe
a) | 50mmØ SWR /PVC WASTE Water PIPE | 1 | 12.5 |  |  | 12.5 | Rmt
[6 empty] | 13 | Rmt
b) | 75mmØ SWR /PVC WASTE Water PIPE | 1 | 17.5 |  |  | 17.5 | Rmt
[6 empty] | 18 | Rmt
c) | 75mmØ SWR /PVC WASTE Water PIPE&Vent
|  | 1 | 2 |  |  | 2
[6 empty] | 2 | Nos
d) | 110mmØ SWR /PVC SOIL WASTE PIPE | 1 | 20.5 |  |  | 20.5 | Rmt
[6 empty] | 21 | Rmt
e) | 110mmØ SWR /PVC WASTE Water PIPE&Vent
|  | 1 | 2 |  |  | 2
[6 empty] | 2 | Nos
51 | Rain water down take pipes
| 110mm Dia | 6 | 4.35 |  |  | 26.1 | Rmt
[5 empty] | Total | 27 | Rmt
WATER SUPPLY
52 | WASH BASINS
Ground Floor
| Toilet | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
53 | Bottle Trap
Ground Floor
| Toilet | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
54 | Floor Trap
Ground Floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
55 | Two Way Bib Cock
Ground Floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
56 | Long Body Bib Cock
Ground Floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
57 | Stop Cock
Ground Floor
| Toilet | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
58 | Mirror Glass
Ground Floor
| Toilet | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
59 | Towel Ring
Ground Floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
60 | Soap Dish
Ground Floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
61 | Double Towel Bar
Ground Floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
62 | Robe Hook
Ground Floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
63 | Angle Valve
Ground Floor
| Toilet | 1 | 3 |  |  | 3
| Total Qty |  |  |  |  | 3 | Nos
64 | Stain Less Steel Bib Cock
Ground Floor
| Toilet | 1 | 1 |  |  | 1
| Total Qty |  |  |  |  | 1 | Nos
65 | 15mmØ CPVC Line
| Ground Floor | 1 | 18 |  |  | 18 | Rmt
[6 empty] | 18 | Rmt
66 | 20mmØ CPVC Line
| Ground Floor | 1 | 3 |  |  | 3 | Rmt
[6 empty] | 3 | Rmt
67 | 25mmØ CPVC Line
| Ground Floor | 1 | 12 |  |  | 12 | Rmt
[6 empty] | 12 | Rmt
68 | 32mmØ CPVC Line
| Ground Floor | 1 | 8 |  |  | 8 | Rmt
[6 empty] | 8 | Rmt
69 | 40mmØ CPVC Line
| Ground Floor | 1 | 10 |  |  | 10 | Rmt
[6 empty] | 10 | Rmt
69 | 25mmØ CPVC Down Take Pipe
| Ground Floor | 1 | 4.5 |  |  | 4.5 | Rmt
[6 empty] | 5 | Rmt
70 | 25mmØ CPVC UP Take Pipe
| Ground Floor | 1 | 4.5 |  |  | 4.5 | Rmt
[6 empty] | 5 | Rmt
[5 empty] | Total | 22 | Rmt
71 | Gate Valve
| 25mm dia | 1 | 1 |  |  | 1
| 32mm dia | 1 | 1 |  |  | 1
[6 empty] | 2 | Nos
72 | Bronze Ball valve with SS Ball
| 25mm Dia | 1 | 1 |  |  | 1
[6 empty] | 1 | Nos
73 | Syntex Tank
| 1500 Liter Capacity | 1 | 1 |  |  | 1
[6 empty] | 1 | Nos

## Security Extension Dtl
PROPOSED CONSTRUCTION OF SECURITY EXTENSION , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Security Extension
1 | Site levelling |  |  |  |  | 0 | Sqm
[5 empty] | Total | 0 | Sqm
2 | Demolishing R.C.C columns,walls and beams work, VDF Flooring
| Under Security Extension | 1 | 4.8 | 3.5 | 0.15 | 2.52 | Cum
[6 empty] | 3 | Cum
3 | Demolishing Reinforced cement concrete , solling and PCC stone
under exixting FFL PCC (1:4:8)
| F-1 | 2 | 2.1 | 2.1 | 0.1 | 0.882 | Cum
[6 empty] | 1 | Cum
Under Exixting FFL 230mm Thick Soling
| F-1 | 2 | 2.1 | 2.1 | 0.23 | 2.0286 | Cum
[6 empty] | 2 | Cum
| Solling and PCC stone Total Qty. |  |  |  |  | 3 | Cum
4 | Hacking and chipping existing surfaces
| Existing Surface Area | 1 | 3.5 |  | 3.2 | 11.2 | Sqm
[5 empty] | Total | 13 | Sqm
5 | Dismantling doors, windows,Vintilator
| Security Extension | 1 |  |  |  | 1 | No's
[5 empty] | Total | 2 | No's
6 | Earth Work excavation
Under Footing For Stair Case
A) Upto 1.50 M
| F-1 | 2 | 1.8 | 1.8 | 1.5 | 9.72 | Cum
Under RR Masonry
| ALL Round Length | 1 | 12 | 0.53 | 0.7 | 4.452 | Cum
| Total |  |  |  |  | 16 | Cum
Above 1.50 till 3.00 M
| F-1 | 2 | 1.8 | 1.8 | 1.5 | 9.72 | Cum
| Total |  |  |  |  | 11 | Cum
| Total Quantity of Excavation |  |  |  |  | 27 | Cum
7 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 27 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | -3 | Cum
| Sand Cohesion |  |  |  |  | -3 | Cum
| RCC Footing |  |  |  |  | -2 | Cum
| Below FFL Column |  |  |  |  | -1 | Cum
| Plinth Beam |  |  |  |  | -1 | Cum
| Below FFL RR Masonry |  |  |  |  | -4 | Cum
| Back fillingQty |  |  |  |  | 13 | Cum
| Basement Filling | 1 | 4.5 | 3 | 0.3 | 4.05 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | 7 | Cum
| Filling With Available Excavated Earth Considered | 40% | x | 27 |  | 10.8 | Cum
| Disposal of Excavated Earth |  |  |  |  | 16.2 | Cum
8 | PCC (1:4:8)
Under Footing
| F-1 | 2 | 1.8 | 1.8 | 0.1 | 0.648 | Cum
[5 empty] | Total | 0.7128 | Cum
Under RR Masonry
| ALL Round Length | 1 | 12 | 0.38 | 0.1 | 0.456 | Cum
[5 empty] | Total | 0.5016 | Cum
Under Room PCC
| Security Extension | 1 | 4.5 | 2.6 | 0.1 | 1.17 | Cum
| Total |  |  |  | Total | 1.287 | Cum
| Total PCC quantity |  |  |  |  | 3 | Cum
9 | 230mm Thick Soling
Under Room
| Security Extension | 1 | 4.5 | 2.6 | 0.23 | 2.691 | Cum
[5 empty] | Total | 3 | Cum
10 | ATT
| Anti terminate | 1 | 4.5 | 3 |  | 14 | Sqm
[6 empty] | 15 | Sqm
| TOTAL ATT Qty. |  |  |  |  | 15 | Sqm
11 | RR MASONRY
Under RR Masonry
Below NGL
| All Round Length | 1 | 12 | 0.45 | 0.6 | 3.24 | Cum
[6 empty] | 4 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 4 | Cum
12 | Plinth Protection
[6 empty] | 0 | Sqm
[6 empty] | 0 | Sqm
| Total Plinth Protection Qty. |  |  |  |  | 0 | Sqm
13 | R.C.C
a) | Under Footing
| F-1 | 2 | 1.5 | 1.5 | 0.45 | 2.025 | Cum
| Total footings RCC |  |  |  |  | 2 | Cum
b) | RCC Columns
GROUND FLOOR
Below FFL
| C1 | 2 | 0.3 | 0.45 | 2.45 | 0.6615 | Cum
| Total columns RCC (upto FFL) |  |  |  |  | 1 | Cum
RCC for columns(above FFL upto GF)
| C1 | 2 | 0.3 | 0.45 | 3 | 0.81 | Cum
| Total |  |  |  |  | 1 | Cum
| Columns |  | RCC (upto FFL) |  |  | 1 | Cum
| Columns | Ground Floor (Above FFL) |  |  |  | 1 | Cum
[5 empty] | TOTAL | 2 | Cum
c) | Plinth Beam
Horizontal Beams
| PB1 | 2 | 4.5 | 0.23 | 0.3 | 0.621 | Cum
Vertical Beams
| PB2 | 1 | 3.5 | 0.23 | 0.3 | 0.2415 | Cum
| Total |  |  |  |  | 1 | Cum
d) | RCC FOR ROOF BEAMS
Ground Floor
Horizontal Beams
| RB1 | 2 | 4.5 | 0.23 | 0.275 | 0.56925 | Cum
Vertical Beams
| RB2 | 2 | 3.5 | 0.23 | 0.275 | 0.44275 | Cum
[5 empty] | Total | 1 | Cum
| Roof Beams |  | Ground Floor |  | TOTAL | 1 | Cum
e) | Roof Slab
GROUND FLOOR
| Roof Slab | 1 | 4.5 | 3.5 | 0.15 | 2.3625 | Cum
[6 empty] | 3 | Cum
| Roof Slab |  | Ground Floor |  | TOTAL | 3 | Cum
f) | Lintels
|  | 2 | 4.5 | 0.23 | 0.3 | 0.621 | Cum
|  | 1 | 3.5 | 0.23 | 0.3 | 0.2415 | Cum
| Lintels |  | Ground Floor |  | TOTAL | 1 | Cum
g) | CHAJJA's
|  | 1 | 13.2 | 0.6 | 0.075 | 0.594 | Cum
[6 empty] | 1 | Cum
| Chajja's |  | Ground Floor |  | TOTAL | 1 | Cum
RCC Concrete Work
| Total Rcc Qty. All Works Upto Plinth Level. |  |  |  |  | 4 | Cum
| Total Rcc Qty. All Works Above Plinth upto Floor V Level |  |  |  |  | 5 | Cum
| Chajja's&Lintel |  |  |  |  | 2 | Cum
|  |  |  | Grand Total |  | 11 | Cum
14 | Supplying & Fabrication of Reinforcement steel
| Footings- 60 kg/cum |  | 2 | X | 60 | 120 | kg
| Plinth Beam- 150 kg/cum |  | 1 | X | 150 | 150 | kg
| Columns-250 kgs/cum |  | 2 | X | 250 | 500 | kg
| Roof beams-250 kgs/cum |  | 1 | X | 250 | 250 | kg
| Slabs-80 kgs/cum |  | 3 | X | 80 | 240 | kg
| Stair case-100 kgs/cum |  | 0 | X | 100 | 0 | kg
| Lintels etc., -80 kg/cum |  | 1 | X | 80 | 80 | kg
| Chajjas etc., -60 kg/cum |  | 1 | X | 60 | 60 | kg
|  |  | 11 |  |  | 1400 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 70 | kg
[6 empty] | 1470 | KG
[5 empty] | (or) | 2 | MT
15 | SHUTTERING
Under Footing
| F-1 | 2 | 6 |  | 0.45 | 5.4 | Sqm
| Total Foundation Shuttering |  |  |  |  | 6 | Sqm
RCC Columns
Below FFL
| C1 | 2 | 1.5 |  | 2.45 | 7.35 | Sqm
[6 empty] | 8 | Sqm
RCC for columns(above FFL upto GF)
| C1 | 2 | 1.5 |  | 3 | 9 | Sqm
[6 empty] | 10 | Sqm
| Columns Shuttering |  | RCC (upto FFL) |  |  | 8 | Sqm
| Columns Shuttering | Ground Floor For Stiar Case (Above FFL) |  |  |  | 10 | Sqm
|  |  |  | Grand Total |  | 18 | Sqm
Shuttering For Plinth Beam
Horizontal Beams
| PB1 | 2 | 4.5 |  | 0.6 | 5.4 | Sqm
Vertical Beams
| PB2 | 1 | 3.5 |  | 0.6 | 2.1 | Sqm
[6 empty] | 8 | Sqm
Shuttering For Roof Beams
Ground Floor
Horizontal Beams
| RB1 | 2 | 4.5 |  | 0.78 | 7.02 | Sqm
Vertical Beams
| RB2 | 2 | 3.5 |  | 0.78 | 5.46 | Sqm
[6 empty] | 14 | Sqm
| Roof Beams Shuttering |  | Ground Floor |  |  | 14 | Sqm
Shuttering For Roof Slab
GROUND FLOOR
| Roof Slab | 1 | 4.5 | 3 |  | 13.5 | Sqm
[6 empty] | 15 | Sqm
| Shuttering for Slabs |  | Ground Floor |  |  | 15 | Sqm
Shuttering for Lintels
| 0 | 2 | 4.5 |  | 0.8 | 7.2 | Sqm
| Sides | 2 | 3.5 |  | 0.8 | 5.6 | Sqm
[5 empty] | Total | 14 | Sqm
Shuttering for Chajjas
|  | 1 | 13.2 | 0.675 |  | 8.91 | Sqm
[5 empty] | Total | 10 | Sqm
16 | Brick Work
CC-Block Masonry Work
Ground Floor
| Horizontal | 2 | 4.5 | 0.2 | 2.7 | 4.86 | Cum
| Vertical | 1 | 2.6 | 0.2 | 2.7 | 1.404 | Cum
STEPS
| Entrance Steps | 1 | 1.05 | 0.9 | 0.15 | 0.14175 | Cum
|  | 1 | 1.05 | 0.6 | 0.3 | 0.189 | Cum
|  | 1 | 1.05 | 0.3 | 0.45 | 0.14175 | Cum
Deduction
| D3 | 1 | 0.9 | 0.2 | 2.1 | -0.378 | Cum
| W3 | 1 | 1.2 | 0.2 | 1.2 | -0.288 | Cum
| WA | 1 | 2.4 | 0.2 | 1.2 | -0.576 | Cum
| WFA | 2 | 2.6 | 0.2 | 1.2 | -1.248 | Cum
| Total 200mm brick work quantity |  |  |  |  | 5 | Cum
| 200mm Thick Brick Work |  | Ground Floor |  | TOTAL | 5 | Cum
17 | 100mm Brick Wall
Half brick masonry
Ground Floor
| Parapet Wall | 1 | 12 |  | 0.3 | 3.6 | Sqm
| Total 100 mm brick work quantity |  |  |  |  | 4 | Sqm
| 100 mm Brick Work |  | Ground Floor |  | TOTAL | 4 | Sqm
18 | Plastering
External plastering(18mm)
Ground Floor
| All round | 1 | 13 |  | 3 | 39 | Sqm
| Parapet Wall Plastering | 1 | 13 |  | 0.715 | 9.295 | Sqm
Entrance Steps -1
| Sides | 1 | 0.9 |  | 0.45 | 0.405 | Sqm
Deductions of 50% External
| D3 | 0.5 | 0.9 |  | 2.1 | -0.945 | Sqm
| W3 | 0.5 | 1.2 |  | 1.2 | -0.72 | Sqm
| WA | 0.5 | 2.4 |  | 1.2 | -1.44 | Sqm
| WFA | 1 | 2.6 |  | 1.2 | -3.12 | Sqm
[5 empty] | Total | 47 | Sqm
| External plastering |  | Ground Floor |  |  | 47 | Sqm
19 | Internal plastering(15mm)
Ground Floor
| Security Extension | 1 | 14.2 |  | 2.85 | 40.47 | Sqm
Deductions of 50% Internal
| D3 | 0.5 | 0.9 |  | 2.1 | -0.945 | Sqm
| W3 | 0.5 | 1.2 |  | 1.2 | -0.72 | Sqm
| WA | 0.5 | 2.4 |  | 1.2 | -1.44 | Sqm
| WFA | 1 | 2.6 |  | 1.2 | -3.12 | Sqm
[5 empty] | Total | 38 | Sqm
| Internal plastering |  | Ground Floor |  | TOTAL | 38 | Sqm
20 | Ceiling plastering
GROUND FLOOR
| Security Extension | 1 | 4.5 | 2.6 |  | 11.7 | Sqm
Chajja's Plastering
| W3 | 2 | 1.43 | 0.6 |  | 1.716 | Sqm
| Sides | 1 | 2.63 |  | 0.075 | 0.19725 | Sqm
| WA | 2 | 2.63 | 0.6 |  | 3.156 | Sqm
| Sides | 1 | 3.83 |  | 0.075 | 0.28725 | Sqm
| WFA | 4 | 2.83 | 0.6 |  | 6.792 | Sqm
| Sides | 2 | 4.03 |  | 0.075 | 0.6045 | Sqm
[6 empty] | 27 | Sqm
| Ceiling plastering |  | Ground Floor |  | TOTAL | 27 | Sqm
21 | Pointing on stone work
Above NGL
| All Round Length |  |  |  |  | 0 | Sqm
[6 empty] | 0 | Sqm
| Pointing Work |  |  |  | TOTAL | 0 | Sqm
22 | Plaster drip course/water patti
| chajja | 1 | 14.4 |  |  | 14.4 | Rmt
| Parapet Wall Watter Patti | 1 | 12 |  |  | 12 | Rmt
[5 empty] | Total | 29 | Rmt
23 | Flooring
Vitrified flooring tiles
Ground Floor
| Security Extension Office Room | 1 | 4.5 | 2.6 |  | 11.7 | Sqm
[5 empty] | Total | 13 | Sqm
| Vitrified flooring |  | Ground Floor |  | TOTAL | 13 | Sqm
24 | Skirting
| Security Extension Office Room | 1 | 14.2 |  | 0.1 | 1.42 | Sqm
| Vitrified flooring Skirting |  |  |  | Total | 2 | Sqm
25 | 18mm thick gang saw cut mirror polished
Doors & Window Sills
[6 empty] | 0 | Sqm
[6 empty] | 0 | Sqm
[6 empty] | 0 | Sqm
[6 empty] | 0 | Sqm
[5 empty] | Total | 0 | Sqm
|  |  |  | Grand Total |  | 0 | Sqm
26 | Kota Stone Flooring
Ground Floor
For Stair Case Area
Entrance Steps - 1
| Threads | 3 | 1.05 | 0.3 |  | 0.945 | Sqm
| Raiser | 3 | 1.05 |  | 0.15 | 0.4725 | Sqm
[5 empty] | Total | 2 | Sqm
| Kota Stone Flooring |  | Ground Floor |  | TOTAL | 2 | Sqm
27 | Painting
| External painting |  |  |  |  | 47 | Sqm
| Internal painting |  |  |  |  | 65 | Sqm
| Internal&External Paint With White Cement Based Putty |  |  |  |  | 112 | Sqm
| Ceiling painting - White wash | [5 empty] | Sqm
28 | Water Proofing works
First Floor
Terrace Water Proofing
| Terrace | 1 | 5 | 3 |  | 15 | Sqm
[5 empty] | Total | 17 | Sqm
29 | Joinery
Ground Floor
WPC Door Shutter 35mm Thick
[6 empty] | 0 | Sqm
[6 empty] | 0 | Sqm
| shutters |  |  |  | Total | 0 | Sqm
b) WPC Door Frame
Ground Floor
[6 empty] | 0 | Rmt
[6 empty] | 0 | Rmt
| WPC Door Frame |  |  |  | TOTAL | 0 | Rmt
30 | UPVC WINDOWS
Ground Floor
Alluminium Windows
| W3 | 1 | 1.2 |  | 1.5 | 1.8 | Sqm
| WA | 1 | 2.4 |  | 1.2 | 2.88 | Sqm
| WFA | 2 | 2.6 |  | 1.2 | 6.24 | Sqm
|  | 1 | 10.4 |  | 1.2 | 12.48 | Sqm
[5 empty] | Total | 23 | Sqm
| UPVC Windows |  |  |  | Total | 23 | Sqm
31 | Hydraulic Door Closer
|  | 3 |  |  |  | 3 | No's
[6 empty] | 3 | No's
32 | MS Grills For Windows
| MS Grills 20kg/Sqm |  |  |  |  | 0 | KGS
| Convertion (20kg/Sqm) |  |  |  |  | 0 | KGS
33 | Synthatic Enamel Paint
a) Steel surfaces with zinc chromate primer
Windows For MS Grill
[6 empty] | 0 | Sqm
[6 empty] | 0 | Sqm
[6 empty] | 0 | Sqm
[5 empty] | Total | 0 | Sqm
b) Wooden surface with approved primer
[6 empty] | 0 | Sqm
[5 empty] | Total | 0 | Sqm
|  |  |  | Grand Total |  | 0 | Sqm
34 | Rain water down take pipes
| 110mm Dia | 2 | 3.6 |  |  | 7.2 | Rmt
[5 empty] | Total | 8 | Rmt

## Scrap yard bins
PROPOSED CONSTRUCTION OF SCRAP YARD BINS , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Scrap Yard Bins
1 | Site levelling | 1 | 12.5 | 28 |  | 350 | Sqm
[5 empty] | Total | 385 | Sqm
2 | Demolishing R.C.C columns,walls and beams work, VDF Flooring
| Scrap Yard |  |  |  |  | 0 | Cum
[6 empty] | 0 | Cum
3 | Demolishing Reinforced cement concrete , solling and PCC stone
under exixting FFL PCC (1:4:8)
| F-1 |  |  |  |  | 0 | Cum
[6 empty] | 0 | Cum
Under Existing FFL 230mm Thick Soling
| F-1 |  |  |  |  | 0 | Cum
[6 empty] | 0 | Cum
| Solling and PCC stone Total Qty. |  |  |  |  | 0 | Cum
4 | Hacking and chipping existing surfaces
| Existing Surface Area |  |  |  |  | 0 | Sqm
[5 empty] | Total | 0 | Sqm
5 | Drilling suitable holes
| Scrap Yard | 56 |  |  |  | 56 | No's
[5 empty] | Total | 62 | No's
6 | Earth Work excavation
Under Footing For Stair Case
A) Upto 1.50 M
| F-1 | 7 | 1.8 | 1.8 | 1.5 | 34.02 | Cum
Under RR Masonry
| ALL Round Length | 1 | 38 | 0.53 | 0.7 | 14.098 | Cum
| Total |  |  |  |  | 53 | Cum
Above 1.50 till 3.00 M
| F-1 | 7 | 1.8 | 1.8 | 1.5 | 34.02 | Cum
| Total |  |  |  |  | 37 | Cum
| Total Quantity of Excavation |  |  |  |  | 90 | Cum
7 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 90 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | -23 | Cum
| Sand Cohesion |  |  |  |  | -44 | Cum
| RCC Footing |  |  |  |  | -15 | Cum
| Below FFL Column |  |  |  |  | -15 | Cum
| Plinth Beam |  |  |  |  | -7 | Cum
| Below FFL RR Masonry |  |  |  |  | -4 | Cum
| Back fillingQty |  |  |  |  | -18 | Cum
| Basement Filling | 1 | 11.6 | 10 | 1 | 116 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | 8 | Cum
| Filling With Available Excavated Earth Considered | 100% | x | 90 |  | 90 | Cum
| Disposal of Excavated Earth |  |  |  |  | 0 | Cum
8 | PCC (1:4:8)
Under Footing
| F-1 | 7 | 1.8 | 1.8 | 0.1 | 2.268 | Cum
[5 empty] | Total | 2.4948 | Cum
Under RR Masonry
| ALL Round Length | 1 | 38 | 0.38 | 0.1 | 1.444 | Cum
[5 empty] | Total | 1.5884 | Cum
Under Room PCC
| Scrap Yard Bins | 1 | 7.5 | 23 | 0.1 | 17.25 | Cum
| Total |  |  |  | Total | 18.975 | Cum
| Total PCC quantity |  |  |  |  | 23 | Cum
9 | 230mm Thick Soling
Under Room
| Scrap Yard Bins | 1 | 7.5 | 23 | 0.23 | 39.675 | Cum
[5 empty] | Total | 44 | Cum
10 | ATT
| Anti terminate | 1 | 7.5 | 23 |  | 173 | Sqm
[6 empty] | 190 | Sqm
| TOTAL ATT Qty. |  |  |  |  | 190 | Sqm
11 | RR MASONRY
Under RR Masonry
Below NGL
| All Round Length | 1 | 7.5 | 0.45 | 0.6 | 2.025 | Cum
[6 empty] | 2 | Cum
Above NGL
| All Round Length | 1 | 7.5 | 0.38 | 0.62 | 1.767 | Cum
[6 empty] | 2 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 4 | Cum
12 | Plinth Protection
|  | 1 | 38 | 0.75 |  | 29 | Sqm
[6 empty] | 32 | Sqm
| Total Plinth Protection Qty. |  |  |  |  | 32 | Sqm
13 | R.C.C
a) | Under Footing
| F-1 | 21 | 1.2 | 1.2 | 0.45 | 13.608 | Cum
| Total footings RCC |  |  |  |  | 15 | Cum
b) | RCC Pedestal
GROUND FLOOR
Below FFL
| P1 | 21 | 0.3 | 0.3 | 2.5 | 4.725 | Cum
Above FFL
| C1 | 21 | 0.3 | 0.3 | 4.5 | 8.505 | Cum
| Total columns RCC (upto FFL) |  |  |  |  | 15 | Cum
| Columns |  | RCC (upto FFL) |  |  | 15 | Cum
c) | Plinth Beam
Horizontal Beams
| PB1 | 7 | 7.5 | 0.23 | 0.38 | 4.5885 | Cum
Vertical Beams
| PB2 | 1 | 23 | 0.23 | 0.38 | 2.0102 | Cum
| Total |  |  |  |  | 7 | Cum
RCC Concrete Work
| Total Rcc Qty. All Works Upto Plinth Level. |  |  |  |  | 37 | Cum
|  |  |  | Grand Total |  | 37 | Cum
14 | Supplying & Fabrication of Reinforcement steel
| Footings- 60 kg/cum |  | 15 | X | 60 | 900 | kg
| Plinth Beam- 150 kg/cum |  | 7 | X | 150 | 1050 | kg
| Columns-250 kgs/cum |  | 15 | X | 250 | 3750 | kg
| Roof beams-250 kgs/cum |  | 0 | X | 250 | 0 | kg
| Slabs-80 kgs/cum |  | 0 | X | 80 | 0 | kg
| Stair case-100 kgs/cum |  | 0 | X | 100 | 0 | kg
| Lintels etc., -80 kg/cum |  | 0 | X | 80 | 0 | kg
| Chajjas etc., -60 kg/cum |  | 0 | X | 60 | 0 | kg
|  |  | 37 |  |  | 5700 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 285 | kg
[6 empty] | 5985 | KG
[5 empty] | (or) | 6 | MT
15 | SHUTTERING
Under Footing
| F-1 | 21 | 4.8 |  | 0.45 | 45.36 | Sqm
| Total Foundation Shuttering |  |  |  |  | 50 | Sqm
RCC Pedestal
Below FFL
| P1 | 21 | 1.2 |  | 2.5 | 63 | Sqm
Above FFL
| C1 | 21 | 1.2 |  | 4.5 | 113.4 | Sqm
[6 empty] | 69 | Sqm
| Columns Shuttering |  | RCC (upto FFL) |  |  | 69 | Sqm
Shuttering For Plinth Beam
Horizontal Beams
| PB1 | 7 | 7.5 |  | 0.76 | 39.9 | Sqm
Vertical Beams
| PB2 | 1 | 23 |  | 0.76 | 17.48 | Sqm
[6 empty] | 63 | Sqm
16 | Vdf Flooring Shuttering
| Building Material | 1 | 22.76 |  | 0.125 | 2.845 | Sqm
| MS Scrap | 1 | 25.74 |  | 0.125 | 3.2175 | Sqm
| SS Scrap | 1 | 20.76 |  | 0.125 | 2.595 | Sqm
| Aluminium Scrap | 1 | 20.76 |  | 0.125 | 2.595 | Sqm
| Assorted Scrap | 1 | 21.16 |  | 0.125 | 2.645 | Sqm
| Oil & Lubricants | 1 | 21.76 |  | 0.125 | 2.72 | Sqm
[6 empty] | 18 | Sqm
17 | Brick Work
CC-Block Masonry Work
Ground Floor
| Horizontal | 2 | 7.5 | 0.2 | 4.5 | 13.5 | Cum
|  | 5 | 7.5 | 0.2 | 3 | 22.5 | Cum
| Vertical | 1 | 23 | 0.2 | 4.5 | 20.7 | Cum
|  | 1 | 23 | 0.2 | 1.5 | 6.9 | Cum
|  | 21 | 4.5 | 0.2 | 0.5 | 9.45 | Cum
STEPS
| Entrance Steps | 1 | 11.875 | 0.9 | 0.15 | 1.6031 | Cum
|  | 1 | 11.875 | 0.6 | 0.3 | 2.1375 | Cum
|  | 1 | 11.875 | 0.3 | 0.45 | 1.6031 | Cum
| Entrance Steps | 2 | 2.45 | 0.9 | 0.15 | 0.6615 | Cum
|  | 2 | 2.45 | 0.6 | 0.3 | 0.882 | Cum
|  | 2 | 2.45 | 0.3 | 0.45 | 0.6615 | Cum
| Total 200mm brick work quantity |  |  |  |  | 89 | Cum
| 200mm Thick Brick Work |  |  |  | TOTAL | 89 | Cum
18 | 100mm Brick Wall
Half brick masonry
Ground Floor
| Horizontal Wall | 5 | 7.5 |  | 1 | 37.5 | Sqm
| Total 100 mm brick work quantity |  |  |  |  | 41 | Sqm
| 100 mm Brick Work |  |  |  | TOTAL | 41 | Sqm
19 | Plastering
External plastering(18mm)
Ground Floor
| All round | 1 | 38 |  | 4.5 | 171 | Sqm
Entrance Steps
| Sides | 1 | 11.875 |  | 0.45 | 5.3438 | Sqm
Entrance Steps
| Sides | 2 | 2.45 |  | 0.45 | 2.205 | Sqm
[5 empty] | Total | 196 | Sqm
| External plastering |  |  |  |  | 196 | Sqm
20 | Internal plastering(15mm)
Ground Floor
| Building Material | 1 | 22.76 |  | 4.5 | 102.42 | Sqm
| MS Scrap | 1 | 25.74 |  | 4 | 102.96 | Sqm
| SS Scrap | 1 | 20.76 |  | 4 | 83.04 | Sqm
| Aluminium Scrap | 1 | 20.76 |  | 4 | 83.04 | Sqm
| Assorted Scrap | 1 | 21.16 |  | 4 | 84.64 | Sqm
| Oil & Lubricants | 1 | 21.76 |  | 4.5 | 97.92 | Sqm
[5 empty] | Total | 609 | Sqm
| Internal plastering |  |  |  | TOTAL | 609 | Sqm
21 | Flooring
VDF Flooring
Ground Floor
| Building Material | 1 | 7.38 | 4 | 0.125 | 3.69 | Cum
| MS Scrap | 1 | 7.38 | 5.49 | 0.125 | 5.0645 | Cum
| SS Scrap | 1 | 7.38 | 3 | 0.125 | 2.7675 | Cum
| Aluminium Scrap | 1 | 7.38 | 3 | 0.125 | 2.7675 | Cum
| Assorted Scrap | 1 | 7.38 | 3.2 | 0.125 | 2.952 | Cum
| Oil & Lubricants | 1 | 7.38 | 3.5 | 0.125 | 3.2287 | Cum
[5 empty] | Total | 23 | Cum
| VDF Flooring |  |  |  | TOTAL | 23 | Cum
22 | Cutting Grooves and filling with silicon waterproof sealant
| for every 3 m x 4m size area | 1.9167 | 14 | - | - | 26.8333 | RM
[5 empty] | Say | 27 | RM
23 | Laying of Hot top
| Solar Power Inverter | 1 | 7.5 | 23 |  | 172.5 | Sqm
[6 empty] | 190 | Sqm
24 | Skirting
| Building Material | 1 | 22.76 |  | 0.1 | 2.276 | Sqm
| MS Scrap | 1 | 25.74 |  | 0.1 | 2.574 | Sqm
| SS Scrap | 1 | 20.76 |  | 0.1 | 2.076 | Sqm
| Aluminium Scrap | 1 | 20.76 |  | 0.1 | 2.076 | Sqm
| Assorted Scrap | 1 | 21.16 |  | 0.1 | 2.116 | Sqm
| Oil & Lubricants | 1 | 21.76 |  | 0.1 | 2.176 | Sqm
| CC Flooring Skirting |  |  |  | Total | 15 | Sqm
25 | Kota Stone Flooring
Ground Floor
Entrance Steps
| Threads | 3 | 11.875 | 0.3 |  | 10.6875 | Sqm
| Raiser | 3 | 11.875 |  | 0.15 | 5.3438 | Sqm
| Threads | 3 | 2.45 | 0.3 |  | 2.205 | Sqm
| Raiser | 3 | 2.45 |  | 0.15 | 1.1025 | Sqm
[5 empty] | Total | 21 | Sqm
| Kota Stone Flooring |  |  |  | TOTAL | 21 | Sqm
26 | Painting
| External painting |  |  |  |  | 196 | Sqm
| Internal painting |  |  |  |  | 609 | Sqm
27 | Joinery
Ground Floor
MS GATE DOORS
| MS Grill Door | 6 | 2 |  | 2.4 | 28.8 | Sqm
[6 empty] | 29 | Sqm
| shutters |  |  |  | Total | 29 | Sqm
28 | MS Grills Door
| MS Grills 24kg/Sqm | 24 | 29 |  |  | 696 | KGS
| Convertion of (24kg/Sqm) |  |  |  |  | 766 | KGS
29 | Synthatic Enamel Paint
a) Steel surfaces with zinc chromate primer
a) | GATE For MS Grill
| GD | 6 | 2 |  | 2.4 | 28.8 | Sqm
b) | Base Plate
For Details of Base Plate
| Base Plate 20mm Thick | 14 | 0.3 | 0.3 |  | 1.26 | Sqm
| Base Plate 10mm Thick | 14 | 0.25 | 0.3 |  | 1.05 | Sqm
c) | Card
Horizontal sides
| Top Chord 60x60x4.0mm | 7 | 8.33 | 0.24 |  | 13.9944 | Sqm
| Bottom Chord 60x60x4.0mm | 7 | 7.5 | 0.24 |  | 12.6 | Sqm
Vertical sides
| Top Chord 60x60x4.0mm | 1 | 23 | 0.24 |  | 5.52 | Sqm
| Bottom Chord 60x60x4.0mm | 2 | 24.2 | 0.24 |  | 11.616 | Sqm
d) | Bracing
Horizontal sides
| SHS 25x25x3.2mm | 7 | 8.33 | 0.1 |  | 5.831 | Sqm
Vertical sides
| SHS 25x25x3.2mm | 2 | 23 | 0.1 |  | 4.6 | Sqm
e) | Square Hallow Section Column
| Section - 100x100x5mm | 7 | 0.4 |  | 4 | 11.2 | Sqm
f) | Purlins
| Section - 96x48x3.20mm | 11 | 0.3 |  | 25 | 82.5 | Sqm
| Total area |  |  |  |  | 178.9714 | Sqm
| Add : 10% Extra for Other Unforessen Items |  |  |  |  | 18 | Sqm
[5 empty] | Total | 196.9714 | Sqm
28 | Galvanized Iron Sheet (G. I)
| Powder Coated G.I. Sheet Roof | 1 | 8.33 | 24.2 |  | 201.586 | Sqm
| Vertical Partion Sheet | 7 | 7.385 |  | 4 | 206.78 | Sqm
|  | 1 | 23 |  | 4 | 92 | Sqm
[6 empty] | 500 | Sqm
[5 empty] | Total | 500 | Sqm
| Coverstion of kg / Sqm = 43kgs) | 1 | 500 | 43 |  | 21500 | Kgs
21500
[5 empty] | Total | 21500 | Kgs
29 | Structural Steel Works
a) | Anchor Bolts
at FFL Lvl.
| 20mm Dia | 56 |  |  | 0.6 | 33.6 | Rmt
[6 empty] | 36.96 | RMT
| Weight of Steel 2.50KG/Rmt | 1 | 36.96 | X | 2.85 | 105.336
[5 empty] | Total | 105 | KG
For Details of @ '6' Anchored in Existing Column
| 16mm Dia | 56 |  |  | 0.35 | 19.6 | Rmt
[6 empty] | 21.56 | RMT
| Weight of Steel 1.60KG/Rmt | 1 | 21.56 | X | 1.6 | 34.496
[5 empty] | Total | 34 | KG
| Total Weight of Anchor Bolts Weight in kg |  |  |  |  | 139 | KG
b) | Base Plate
For Details of Base Plate
| Base Plate 20mm Thick | 14 | 0.3 | 0.3 |  | 1.26 | Sqm
[5 empty] | Total | 1.26 | Sqm
| For 1SQM (314.00/2=157KG) |  | 157 |  |  | 218 | Kg
For Details of @ '6' Anchored in Existing Compound Wall
For Details of Base Plate
| Base Plate 10mm Thick | 14 | 0.25 | 0.3 |  | 1.05 | Sqm
[5 empty] | Total | 1.05 | Sqm
| For 1SQM (157.00/2=78.50KG) |  | 78.5 |  |  | 91 | Kg
| Total Weight of Base Plate Weight in kg |  |  |  |  | 309 | KG
c) | Card
Horizontal sides
Top card 60x60x4.0mm
| Top Chord 60x60x4.0mm | 7 | 8.33 |  |  | 58.31 | Rmt
[6 empty] | 64.141 | RMT
| Weight of Steel 4.20KG/Rmt | 1 | 64.141 | X | 4.2 | 269.3922
[5 empty] | Total | 269 | KG
Bottom Card 60x60x4.0mm
| Top Chord 60x60x4.0mm | 7 | 7.5 |  |  | 52.5 | Rmt
[6 empty] | 57.75 | RMT
| Weight of Steel 4.20KG/Rmt | 1 | 57.75 | X | 4.2 | 242.55
[5 empty] | Total | 243 | KG
Vertical sides
Top Card 60x60x4.0mm
| Top Chord 60x60x4.0mm | 1 | 23 |  |  | 23 | Rmt
[6 empty] | 25.3 | RMT
| Weight of Steel 4.20KG/Rmt | 1 | 25.3 | X | 4.2 | 106.26
[5 empty] | Total | 106 | KG
Bottom Card 60x60x4.0mm
| Top Chord 60x60x4.0mm | 2 | 24.2 |  |  | 48.4 | Rmt
[6 empty] | 53.24 | RMT
| Weight of Steel 4.20KG/Rmt | 1 | 53.24 | X | 4.2 | 223.608
[5 empty] | Total | 224 | KG
| Total Weight of Chord Weight in kg |  |  |  |  | 842 | KG
d) | Bracing
Horizontal sides
| SHS 25x25x3.2mm | 7 | 8.33 |  |  | 58.31 | Rmt
[6 empty] | 64.141 | RMT
| Weight of Steel 1.98KG/Rmt | 1 | 64.141 | X | 1.98 | 126.9992
[5 empty] | Total | 127 | KG
Vertical sides
| SHS 25x25x3.2mm | 2 | 23 |  |  | 46 | Rmt
[6 empty] | 50.6 | RMT
| Weight of Steel 1.98KG/Rmt | 1 | 50.6 | X | 1.98 | 100.188
[5 empty] | Total | 100 | KG
| Total Weight of Bracing Weight in kg |  |  |  |  | 227 | KG
e) | Square Hallow Section Column
| Section - 100x100x5mm | 7 |  |  | 4 | 28 | Rmt
[6 empty] | 30.8 | RMT
| Weight of Steel 14.41KG/Rmt | 1 | 30.8 | X | 14.41 | 443.828
[5 empty] | Total | 444 | KG
| Total Weight of Square Section Column Weight in kg |  |  |  |  | 444 | KG
| Add : 10% Extra for Other Unforessen Items |  |  |  |  | 44 | kg
| Grand Total Weight of Structural Steel Work |  |  |  |  | 2632 | KG
f) | Purlins
| Section - 96x48x3.20mm | 11 |  |  | 25 | 275 | Rmt
[6 empty] | 302.5 | RMT
| Weight of Steel 14.41KG/Rmt | 1 | 302.5 | X | 6.71 | 2029.775
[5 empty] | Total | 2030 | KG
| Total Weight of Square Section Column Weight in kg |  |  |  |  | 2030 | KG
| Add : 10% Extra for Other Unforessen Items |  |  |  |  | 203 | kg
| Grand Total Weight of Structural Steel Work |  |  |  |  | 2233 | KG
30 | Gutter (600 mm over all girth)
| Gutter | 1 | 25 |  |  | 25 | Rmt
[6 empty] | 28 | RMT
31 | Rain water down take pipes
| 110mm Dia | 6 | 4.1 |  |  | 24.6 | Rmt
[5 empty] | Total | 25 | Rmt

## Oil Store
PROPOSED CONSTRUCTION OF OIL STORE (FIRST FLOOR ONLY) BUILDING PROPOSED FIRST FLOOR , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Oil Store
1 | Site levelling | 0 | 5.5 | 10 |  | 0 | Sqm
[5 empty] | Total | 0 | Sqm
2 | Earth Work excavation
Under Footing For Stair Case
A) Upto 1.50 M
| F-2 | 0 | 2.1 | 2.1 | 1.5 | 0 | Cum
Under RR Masonry
| ALL Round Length | 0 | 9.8 | 0.53 | 0.7 | 0 | Cum
| Total |  |  |  |  | 0 | Cum
Above 1.50 till 3.00 M
| F-2 | 0 | 2.1 | 2.1 | 1 | 0 | Cum
| Total |  |  |  |  | 0 | Cum
| Total Quantity of Excavation |  |  |  |  | 0 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 0 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | 0 | Cum
| Sand Cohesion |  |  |  |  | 0 | Cum
| RCC Footing |  |  |  |  | 0 | Cum
| Below FFL Column |  |  |  |  | 0 | Cum
| Plinth Beam |  |  |  |  | 0 | Cum
| Below FFL RR Masonry |  |  |  |  | 0 | Cum
| Back fillingQty |  |  |  |  | 0 | Cum
| Basement Filling | 0 | 3 | 5 | 1 | 0 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | 0 | Cum
| Filling With Available Excavated Earth Considered | 0% | x | 0 |  | 0 | Cum
| Disposal of Excavated Earth |  |  |  |  | 0 | Cum
4 | PCC (1:4:8)
Under Footing PCC For Stair Case
| F-2 | 0 | 1.95 | 1.95 | 0.1 | 0 | Cum
[5 empty] | Total | 0 | Cum
Under RR Masonry
| ALL Round Length | 0 | 9.8 | 0.38 | 0.1 | 0 | Cum
[5 empty] | Total | 0 | Cum
Under Room PCC
| Stair Case Area | 0 | 3 | 5 | 0.1 | 0 | Cum
| Total |  |  |  | Total | 0 | Cum
| Total PCC quantity |  |  |  |  | 0 | Cum
5 | 230mm Thick Soling
Under Room
| Stair Case Area | 0 | 3 | 5 | 0.23 | 0 | Cum
[5 empty] | Total | 0 | Cum
6 | ATT
| Anti terminate | 0 | 3 | 5.575 |  | 0 | Sqm
[6 empty] | 0 | Sqm
| TOTAL ATT Qty. |  |  |  |  | 0 | Sqm
7 | RR MASONRY
Under RR Masonry For Stair Case
Below NGL
| All Round Length | 0 | 9.8 | 0.45 | 0.6 | 0 | Cum
[6 empty] | 0 | Cum
Above NGL
| All Round Length | 0 | 9.8 | 0.38 | 0.7 | 0 | Cum
[6 empty] | 0 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 0 | Cum
8 | Plinth Protection
|  | 0 | 11 | 0.75 |  | 0 | Sqm
[6 empty] | 0 | Sqm
| Total Plinth Protection Qty. |  |  |  |  | 0 | Sqm
9 | R.C.C
a) | Under Footing For Stair Case
| F-2 | 0 | 1.8 | 1.8 | 0.55 | 0 | Cum
| Total footings RCC |  |  |  |  | 0 | Cum
b) | RCC Columns
GROUND FLOOR
Below FFL For Stiar Case
| C2 | 0 | 0.23 | 0.45 | 2.55 | 0 | Cum
| Total columns RCC (upto FFL) |  |  |  |  | 0 | Cum
RCC for columns(above FFL upto GF) For Stair Case
| C2 | 0 | 0.23 | 0.45 | 3 | 0 | Cum
| Total |  |  |  |  | 0 | Cum
FIRST FLOOR
RCC Coulmn For First Floor
| C1 | 8 | 0.23 | 0.45 | 3.3 | 2.7324 | Cum
| Total |  |  |  |  | 3 | Cum
Head Room
RCC Coulmn For Head Room
| C1 | 0 | 0.23 | 0.45 | 2.8 | 0 | Cum
| Total |  |  |  |  | 0 | Cum
| Columns |  | RCC (upto FFL) |  |  | 0 | Cum
| Columns | Ground Floor For Stiar Case (Above FFL) |  |  |  | 0 | Cum
| Columns |  | First Floor |  |  | 3 | Cum
| Columns |  | Head Room Floor |  |  | 0 | Cum
[5 empty] | TOTAL | 3 | Cum
c) | Plinth Beam
Horizontal Beams
| PB1 | 0 | 3 | 0.23 | 0.3 | 0 | Cum
Vertical Beams
| PB1 | 0 | 5.75 | 0.23 | 0.3 | 0 | Cum
| Total |  |  |  |  | 0 | Cum
d) | RCC FOR ROOF BEAMS
Ground Floor For Stair Case
Horizontal Beams
| RB1 | 0 | 3 | 0.23 | 0.425 | 0 | Cum
Vertical Beams
| RB2 | 0 | 5.75 | 0.23 | 0.425 | 0 | Cum
[5 empty] | Total | 0 | Cum
FIRST FLOOR
Horizontal Beams
| RB1 | 2 | 14.16 | 0.23 | 0.425 | 2.7683 | Cum
Vertical Beams
| RB2 | 3 | 6.64 | 0.23 | 0.425 | 1.9472 | Cum
[5 empty] | Total | 5 | Cum
HEAD ROOM FLOOR
Horizontal Beams
| RB1 | 0 | 3 | 0.23 | 0.425 | 0 | Cum
Vertical Beams
| RB2 | 0 | 6.64 | 0.23 | 0.425 | 0 | Cum
[5 empty] | Total | 0 | Cum
| Roof Beams |  | Ground Floor |  | TOTAL | 0 | Cum
| Roof Beams |  | First Floor |  | TOTAL | 5 | Cum
| Roof Beams |  | Head Room Floor |  | TOTAL | 0 | Cum
|  |  |  | Grand Total |  | 5 | Cum
e) | Roof Slab
FIRST FLOOR
| Oil Store | 1 | 14.16 | 6.64 | 0.125 | 11.7528 | Cum
[6 empty] | 12 | Cum
HEAD ROOM FLOOR
| Head Room Roof Area | 0 | 3 | 6.64 | 0.125 | 0 | Cum
[6 empty] | 0 | Cum
| Roof Slab |  | First Floor |  | TOTAL | 12 | Cum
| Roof Slab |  | Head Room Floor |  | TOTAL | 0 | Cum
|  |  |  | Grand Total |  | 12 | Cum
STAIRCASE CONCRETING
Ground Floor
Staircase-1
| Waist slab First Flight | 0 | 6 | 1.5 | 0.175 | 0 | Cum
| Steps | 0 | 1.2 | 0.3 | 0.15 | 0 | Cum
| Midlanding | 0 | 3 | 1.5 | 0.175 | 0 | Cum
| Mid Landing Beam | 0 | 2.17 | 0.23 | 0.475 | 0 | Cum
[6 empty] | 0 | Cum
First Floor
Staircase-1
| Waist slab First Flight | 0 | 6 | 1.5 | 0.175 | 0 | Cum
| Steps | 0 | 1.2 | 0.3 | 0.15 | 0 | Cum
| Midlanding | 0 | 3 | 1.5 | 0.175 | 0 | Cum
| Mid Landing Beam | 0 | 2.17 | 0.23 | 0.475 | 0 | Cum
[6 empty] | 0 | Cum
| Staircase |  | Ground Floor |  | TOTAL | 0 | Cum
| Staircase |  | First Floor |  | TOTAL | 0 | Cum
|  |  |  | Grand Total |  | 0 | Cum
f) | Lintels
For Stair Case
| D1 | 0 | 1.28 | 0.23 | 0.25 | 0 | Cum
| W1 | 0 | 1.73 | 0.23 | 0.25 | 0 | Cum
First Floor
| W1 | 1 | 41.6 | 0.2 | 0.35 | 2.912 | Cum
| Lintels |  | G+1 Floor |  | TOTAL | 3 | Cum
g) | CHAJJA's
For Stair Case
| W1 | 0 | 1.73 | 0.6 | 0.075 | 0 | Cum
First Floor
| W1 | 1 | 41.6 | 0.6 | 0.075 | 1.872 | Cum
[6 empty] | 2 | Cum
| Chajja's |  | G+1 Floor |  | TOTAL | 2 | Cum
RCC Concrete Work
| Total Rcc Qty. All Works Upto Plinth Level. |  |  |  |  | 0 | Cum
| Total Rcc Qty. All Works Above Plinth upto Floor V Level |  |  |  |  | 20 | Cum
| Chajja's&Lintel |  |  |  |  | 5 | Cum
|  |  |  | Grand Total |  | 25 | Cum
10 | Supplying & Fabrication of Reinforcement steel
| Footings- 60 kg/cum |  | 0 | X | 60 | 0 | kg
| Plinth Beam- 150 kg/cum |  | 0 | X | 150 | 0 | kg
| Columns-250 kgs/cum |  | 3 | X | 250 | 750 | kg
| Roof beams-250 kgs/cum |  | 5 | X | 250 | 1250 | kg
| Slabs-80 kgs/cum |  | 12 | X | 80 | 960 | kg
| Stair case-100 kgs/cum |  | 0 | X | 100 | 0 | kg
| Lintels etc., -80 kg/cum |  | 3 | X | 80 | 240 | kg
| Chajjas etc., -60 kg/cum |  | 2 | X | 60 | 120 | kg
|  |  | 25 |  |  | 3320 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 166 | kg
[6 empty] | 3486 | KG
[5 empty] | (or) | 4 | MT
11 | SHUTTERING
Under Footing For Stair Case
| F-2 | 0 | 7.2 |  | 0.55 | 0 | Sqm
| Total Foundation Shuttering |  |  |  |  | 0 | Sqm
RCC Columns
Below FFL For Stiar Case
| C2 | 0 | 1.36 |  | 2.55 | 0 | Sqm
[6 empty] | 0 | Sqm
RCC for columns(above FFL upto GF) For Stair Case
| C2 | 0 | 1.36 |  | 3 | 0 | Sqm
[6 empty] | 0 | Sqm
FIRST FLOOR
RCC Coulmn For First Floor
| C1 | 8 | 1.36 |  | 3.3 | 35.904 | Sqm
[6 empty] | 38 | Sqm
Head Room
RCC Coulmn For Head Room
| C1 | 0 | 1.36 |  | 2.8 | 0 | Sqm
[6 empty] | 0 | Sqm
| Columns Shuttering |  | RCC (upto FFL) |  |  | 0 | Sqm
| Columns Shuttering | Ground Floor For Stiar Case (Above FFL) |  |  |  | 0 | Sqm
| Columns Shuttering |  | First Floor |  |  | 38 | Sqm
| Columns Shuttering |  | Head Room Floor |  |  | 0 | Sqm
|  |  |  | Grand Total |  | 38 | Sqm
Shuttering For Plinth Beam
Horizontal Beams
| PB1 | 0 | 3 |  | 0.6 | 0 | Sqm
Vertical Beams
| PB1 | 0 | 5.75 |  | 0.6 | 0 | Sqm
[6 empty] | 0 | Sqm
Shuttering For Roof Beams
Ground Floor For Stair Case
Horizontal Beams
| RB1 | 0 | 3 |  | 1.08 | 0 | Sqm
Vertical Beams
| RB2 | 0 | 5.75 |  | 1.08 | 0 | Sqm
[6 empty] | 0 | Sqm
FIRST FLOOR
Horizontal Beams
| RB1 | 2 | 14.16 |  | 1.08 | 30.5856 | Sqm
Vertical Beams
| RB2 | 3 | 6.64 |  | 1.08 | 21.5136 | Sqm
[6 empty] | 55 | Sqm
HEAD ROOM FLOOR
Horizontal Beams
| RB1 | 0 | 3 |  | 1.08 | 0 | Sqm
Vertical Beams
| RB2 | 0 | 6.64 |  | 1.08 | 0 | Sqm
[6 empty] | 0 | Sqm
| Roof Beams Shuttering |  | Ground Floor |  |  | 0 | Sqm
| Roof Beams Shuttering |  | First Floor |  |  | 55 | Sqm
| Roof Beams Shuttering |  | Head Room |  |  | 0 | Sqm
|  |  |  | Grand Total |  | 55 | Sqm
Shuttering For Roof Slab
FIRST FLOOR
| Oil Store | 1 | 14.16 | 6.64 |  | 94.0224 | Sqm
[6 empty] | 99 | Sqm
HEAD ROOM FLOOR
| Head Room Roof Area | 0 | 3 | 6.64 |  | 0 | Sqm
[6 empty] | 0 | Sqm
| Shuttering for Slabs |  | First Floor |  |  | 99 | Sqm
| Shuttering for Slabs |  | Head Room |  |  | 0 | Sqm
|  |  |  | Grand Total |  | 99 | Sqm
Shuttering For Stair Case
Ground Floor
Staircase-1
| Waist slab First Flight | 0 | 6 | 1.5 |  | 0 | Sqm
| Steps | 0 | 1.2 | 0.15 |  | 0 | Sqm
| Midlanding | 0 | 3 | 1.5 |  | 0 | Sqm
| Mid Landing Beam | 0 | 2.17 | 1.18 |  | 0 | Sqm
[6 empty] | 0 | Sqm
First Floor
Staircase-1
| Waist slab First Flight | 0 | 6 | 1.5 |  | 0 | Sqm
| Steps | 0 | 1.2 | 0.15 |  | 0 | Sqm
| Midlanding | 0 | 3 | 1.5 |  | 0 | Sqm
| Mid Landing Beam | 0 | 2.17 | 1.18 |  | 0 | Sqm
[6 empty] | 0 | Sqm
| Staircase |  | Ground Floor |  |  | 0 | Sqm
| Staircase |  | First Floor |  |  | 0 | Sqm
|  |  |  | Grand Total |  | 0 | Sqm
Shuttering for Lintels
| D1 | 0 | 1.28 | 0.23 |  | 0 | Sqm
| Sides | 0 | 1.28 |  | 0.73 | 0 | Sqm
| W1 | 1 | 41.6 | 0.2 |  | 8.32 | Sqm
|  | 1 | 41.6 |  | 0.9 | 37.44 | Sqm
[5 empty] | Total | 48 | Sqm
Shuttering for Chajjas
| W1 | 0 | 1.73 | 0.6 |  | 0 | Sqm
| Sides | 0 | 2.93 |  | 0.075 | 0 | Sqm
| W1 | 1 | 41.6 | 0.6 |  | 24.96 | Sqm
| Sides | 1 | 42.8 |  | 0.075 | 3.21 | Sqm
[5 empty] | Total | 30 | Sqm
12 | Brick Work
CC-Block Masonry Work
Ground Floor
For Stair Case
| Horizontal | 0 | 2.4 | 0.23 | 2.575 | 0 | Cum
| Vertical | 0 | 5.44 | 0.23 | 2.575 | 0 | Cum
STEPS
| Entrance Steps -1 | 0 | 0.9 | 0.9 | 0.2 | 0 | Cum
|  | 0 | 0.9 | 0.6 | 0.4 | 0 | Cum
|  | 0 | 0.9 | 0.3 | 0.6 | 0 | Cum
| Landing | 0 | 1.2 | 1 | 0.6 | 0 | Cum
For Stair Case
| Flight-1 | 0 | 1.2 | 0.3 | 0.15 | 0 | Cum
| Flight-2 | 0 | 1.2 | 0.3 | 0.15 | 0 | Cum
| Total 200 mm brick work quantity |  |  |  |  | 0 | Cum
FIRST FLOOR
| Horizontal-1 | 2 | 12.5 | 0.2 | 3.175 | 15.875 | Cum
| Vertical -1 | 2 | 5 | 0.2 | 3.175 | 6.35 | Cum
For Stair Case
| Flight-1 | 0 | 1.2 | 0.3 | 0.15 | 0 | Cum
| Flight-2 | 0 | 1.2 | 0.3 | 0.15 | 0 | Cum
Deductions
| D1 | 1 | 1.2 | 0.2 | 2.1 | -0.504 | Cum
| W5 | 8 | 1.5 | 0.2 | 1.2 | -2.88 | Cum
[6 empty] | 20 | Cum
HEAD ROOM FLOOR
| Horizontal-1 | 0 | 2.4 | 0.2 | 2.3 | 0 | Cum
| Vertical -1 | 0 | 5 | 0.2 | 2.3 | 0 | Cum
Deductions
| D1 | 0 | 1 | 0.2 | 2.1 | 0 | Cum
[6 empty] | 0 | Cum
| 200mm Thick Brick Work |  | Ground Floor |  | TOTAL | 0 | Cum
| 200mm Thick Brick Work |  | First Floor |  | TOTAL | 20 | Cum
| 200mm Thick Brick Work |  | Head Room |  | TOTAL | 0 | Cum
|  |  |  | Grand Total |  | 20 | Cum
13 | 100mm Brick Wall
Half brick masonry
First Floor
| Parapet Wall | 2 | 38.8 |  | 0.9 | 69.84 | Sqm
Deductions
| Total 100mm brick work quantity |  |  |  |  | 73 | Sqm
| 100 mm Brick Work |  | Ground Floor |  | TOTAL | 73 | Sqm
14 | Plastering
External plastering(18mm)
Ground Floor
| For Stair Case | 0 | 9.8 |  | 3.6 | 0 | Sqm
Entrance Steps -1
| Sides | 0 | 0.9 |  | 0.6 | 0 | Sqm
[5 empty] | Total | 0 | Sqm
First Floor
| All round | 1 | 38.8 |  | 3.6 | 139.68 | Sqm
| Parapet Wall Plastering | 1 | 38.8 |  | 1.915 | 74.302 | Sqm
Deductions of 50% External
| D1 | 0.5 | 1.2 |  | 2.1 | -1.26 | Sqm
| W1 | 4 | 1.5 |  | 1.5 | -9 | Sqm
[5 empty] | Total | 214 | Sqm
Head Room Floor
| All round | 0 | 18.88 |  | 2.8 | 0 | Sqm
[5 empty] | Total | 0 | Sqm
| External plastering |  | Ground Floor |  |  | 0 | Sqm
| External plastering |  | First Floor |  |  | 214 | Sqm
| External plastering |  | Head Room |  |  | 0 | Sqm
|  |  |  | Grand Total |  | 214 | Sqm
15 | Internal plastering(15mm)
Ground Floor
| For Stair Case Area | 0 | 17.5 |  | 3.6 | 0 | Sqm
[5 empty] | Total | 0 | Sqm
First Floor
| Oil Store | 1 | 37.12 |  | 3.475 | 128.992 | Sqm
| For Stair Case | 1 | 17.5 |  | 3.475 | 60.8125 | Sqm
Deductions of 50% Internal
| D1 | 0.5 | 1.2 |  | 2.1 | -1.26 | Sqm
| W5 | 4 | 1.5 |  | 1.5 | -9 | Sqm
[5 empty] | Total | 189 | Sqm
Head Room Floor
| Head Room Area | 1 | 14.8 |  | 2.675 | 39.59 | Sqm
[5 empty] | Total | 42 | Sqm
| Internal plastering |  | Ground Floor |  | TOTAL | 0 | Sqm
| Internal plastering |  | First Floor |  | TOTAL | 189 | Sqm
| Internal plastering |  | Head Room |  | TOTAL | 42 | Sqm
|  |  |  | Grand Total |  | 231 | Sqm
16 | Ceiling plastering
GROUND FLOOR
Staircase
| Waist slab First Flight | 0 | 6 | 1.5 |  | 0 | Sqm
| Midlanding | 0 | 3 | 1.5 |  | 0 | Sqm
[6 empty] | 0 | Sqm
FIRST FLOOR
| Oil Store | 1 | 11.2 | 5.6 |  | 62.72 | Sqm
Staircase
| Waist slab First Flight | 1 | 6 | 1.5 |  | 9 | Sqm
| Midlanding | 1 | 3 | 1.5 |  | 4.5 | Sqm
Chajja's Plastering
| W1 | 1 | 42 | 0.6 |  | 25.2 | Sqm
| Sides | 1 | 43.2 |  | 0.075 | 3.24 | Sqm
[6 empty] | 110 | Sqm
HEAD ROOM FLOOR
| Head Room Roof Area | 1 | 3 | 5 |  | 15 | Sqm
[6 empty] | 16 | Sqm
| Ceiling plastering |  | Ground Floor |  | TOTAL | 0 | Sqm
| Ceiling plastering |  | First Floor |  | TOTAL | 110 | Sqm
| Ceiling plastering |  | Head Room |  | TOTAL | 16 | Sqm
|  |  |  | Grand Total |  | 126 | Sqm
17 | Pointing on stone work
Above NGL
| All Round Length | 0 | 9.8 |  | 0.7 | 0 | Sqm
[6 empty] | 0 | Sqm
| Pointing Work |  |  |  | TOTAL | 0 | Sqm
18 | Plaster drip course/water patti
First Floor
| W1 | 1 | 43.2 |  |  | 43.2 | Rmt
| Parapet Wall Watter Patti | 1 | 37.4 |  |  | 37.4 | Rmt
[5 empty] | Total | 85 | Rmt
19 | Flooring
Vitrified Floor Tiles
First Floor
| oil store | 1 | 12.6 | 5.6 |  | 70.56 | Sqm
[5 empty] | Total | 78 | Sqm
| Vitrified Flooring |  | First Floor |  | TOTAL | 78 | Sqm
20 | Skirting
| oil store | 1 | 36.4 |  | 0.1 | 3.64 | Sqm
| Vitrified Flooring Skirting |  |  |  | Total | 4 | Sqm
21 | 18mm thick gang saw cut mirror polished
Doors & Window Sills
| D1 | 1 | 1.2 | 0.2 |  | 0.24 | Sqm
| W1 | 8 | 1.5 | 0.2 |  | 2.4 | Sqm
[5 empty] | Total | 3 | Sqm
|  |  |  | Grand Total |  | 3 | Sqm
22 | Kota Stone Flooring
Ground Floor
For Stair Case Area
Entrance Steps - 1
| Threads | 0 | 0.9 | 0.3 |  | 0 | Sqm
| Raiser | 0 | 1.2 |  | 0.15 | 0 | Sqm
| Steps Landing | 0 | 2.4 | 1.73 |  | 0 | Sqm
| Open Area | 0 | 2.4 | 2.93 |  | 0 | Sqm
| Open Area | 0 | 1.2 | 0.9 |  | 0 | Sqm
Stair Case
Flight
| Thread | 0 | 1.5 | 0.3 |  | 0 | Sqm
| Raiser | 0 | 1.5 |  | 0.15 | 0 | Sqm
| Landing | 0 | 2.4 | 1.2 |  | 0 | Sqm
[5 empty] | Total | 0 | Sqm
First Floor
Stair Case
Flight
| Thread | 20 | 1.5 | 0.3 |  | 9 | Sqm
| Raiser | 20 | 1.5 |  | 0.15 | 4.5 | Sqm
| Landing | 1 | 3 | 1.2 |  | 3.6 | Sqm
| open space Area Balcony | 1 | 3 | 2.5 |  | 7.5 | Sqm
[5 empty] | Total | 26 | Sqm
| Kota Stone Flooring |  | Ground Floor |  | TOTAL | 0 | Sqm
| Kota Stone Flooring |  | First Floor |  | TOTAL | 26 | Sqm
|  |  |  | Grand Total |  | 26 | Sqm
23 | Painting
| External painting |  |  |  |  | 214 | Sqm
| Internal painting |  |  |  |  | 231 | Sqm
| Internal&External Paint With White Cement Based Putty |  |  |  |  | 445 | Sqm
| Ceiling painting - White wash |  |  |  |  | 126 | Sqm
24 | Water Proofing works
First Floor
Terrace Water Proofing
| Terrace | 1 | 14.2 | 6.64 |  | 94.288 | Sqm
[5 empty] | Total | 99 | Sqm
25 | Joinery
First Floor
WPC Door Shutter 35mm Thick
| D1 | 1 | 1.2 |  | 2.1 | 2.52 | Sqm
[6 empty] | 3 | Sqm
| shutters |  |  |  | Total | 3 | Sqm
b) WPC Door Frame
First Floor
| D1 | 1 | 5.4 |  |  | 5.4 | Rmt
[6 empty] | 5 | Rmt
| WPC Door Frame |  |  |  | TOTAL | 5 | Rmt
26 | UPVC WINDOWS
First Floor
UPVC WINDOWS
| W1 | 0 | 1.5 |  | 1.5 | 0 | Sqm
[5 empty] | Total | 0 | Sqm
| UPVC WINDOWS |  |  |  | Total | 0 | Sqm
27 | Hydraulic Door Closer
| D1 | 2 |  |  |  | 2 | No's
[6 empty] | 2 | No's
27 | S.S Railing
Ground Floor
Stair Case
| Waist slab Flight | 0 | 6 |  | 0.9 | 0 | Sqm
[6 empty] | 0 | Sqm
First Floor
Stair Case
| Waist slab Flight | 0 | 6 |  | 0.9 | 0 | Sqm
| Balcony | 0 | 38.4 |  | 0.9 | 0 | Sqm
[6 empty] | 0 | Sqm
|  |  |  | Grand Total |  | 0 | Sqm
| SS TUBES 25KGS /Sqm | 25 |  |  |  | 0 | KGS
28 | MS Grills For Windows
| MS Grills 20kg/Sqm | 0 | 0 |  |  | 0 | KGS
| Convertion (20kg/Sqm) |  |  |  |  | 0 | KGS
29 | Synthatic Enamel Paint
a) Steel surfaces with zinc chromate primer
Windows For MS Grill
| W5 | 0 | 1.5 |  | 1.5 | 0 | Sqm
[5 empty] | Total | 0 | Sqm
b) Wooden surface with approved primer
| D1 | 1 | 1.2 |  | 2.1 | 2.52 | Sqm
[5 empty] | Total | 3 | Sqm
|  |  |  | Grand Total |  | 3 | Sqm
30 | Rain water down take pipes
| 110mm Dia | 3 | 3.75 |  |  | 11.25 | Rmt
[5 empty] | Total | 12 | Rmt

## Parking Shed Dtl.
PROPOSED CONSTRUCTION OF PARKING SHED , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Parking Shed
A | PARKING SHED -1&2 (Both side Two Wheeler Parking)
1 | Galvanized Iron Sheet (G. I)
| Powder Coated G.I.Roof Sheet | 2 | 5.1 | 50.04 |  | 510.408 | Sqm
[6 empty] | 510 | Sqm
| Powder Coated G.I. Roof Sheet Qty. Shed -1&2 |  |  |  | Total | 561 | Sqm
2 | Structural Steel Works
a | ISMB - 200 | 20 | 3.6 |  |  | 72 | Rmt
[5 empty] | Total | 72 | Rmt
| ISMB -200- 25.4Rmt/Kg |  | 25.4 |  |  | 2012 | Kgs
b | ISMC -150 2no's | 4 | 50 |  |  | 200 | Rmt
[5 empty] | Total | 200 | Rmt
| ISMC - 150- 16.4Kg/Rmt |  | 16.4 |  |  | 3608 | Kgs
c | Base Plate
Base Plate -250x300x16mm thick
| Base Plate 16mm Thick | 40 | 0.3 | 0.25 |  | 3 | Sqm
[5 empty] | Total | 3 | Sqm
| For 1SQM (251.2/2=125.60KG) |  | 125.6 |  |  | 414 | Kg
| Total Weight of Base Plate Weight in kg Shed -1&2 |  |  |  |  | 414 | KG
d | Card
Top Card 50x50x3.6mm
| Top Card 50x50x3.6mm | 20 | 5.1 |  |  | 102 | Rmt
[6 empty] | 112.2 | Rmt
| Weight of Steel 4.98KG/Rmt | 1 | 112.2 | X | 4.98 | 558.756
[5 empty] | Total | 615 | KG
Bottom Card 50x50x3.6mm
| Bottom Card 50x50x3.6mm | 20 | 5 |  |  | 100 | Rmt
[6 empty] | 110 | RMT
| Weight of Steel 4.98KG/Rmt | 1 | 110 | X | 4.98 | 547.8
[5 empty] | Total | 603 | KG
| Total Weight of Card Weight in kg Shed -1&2 |  |  |  |  | 1218 | KG
e | Web Members
Web Members 25x25x3.2mm
| 25x25x3.2mm | 20 | 11.796 |  |  | 235.92 | Rmt
[6 empty] | 259.512 | RMT
| Weight of Steel 1.98KG/Rmt | 1 | 259.512 | X | 1.98 | 513.8338
[5 empty] | Total | 565 | KG
| Total Weight of Web Members Weight in kg Shed - 1&2 |  |  |  |  | 565 | KG
f | Bracings
| SHS Bracings 25x25x3.2mm | 20 | 9.44 |  |  | 188.8 | Rmt
[6 empty] | 207.68 | RMT
| Weight of Steel 1.98KG/Rmt | 1 | 207.68 | X | 1.98 | 411.2064
[5 empty] | Total | 452 | KG
| Total Weight of Bracing Weight in kg Shed - 1&2 |  |  |  |  | 452 | KG
g | Lacing
Web Members 50x25x3.2mm
| 50x25x3.2mm | 40 | 5 |  |  | 200 | Rmt
[6 empty] | 220 | RMT
| Weight of Steel 3.24KG/Rmt | 1 | 220 | X | 3.24 | 712.8
[5 empty] | Total | 784 | KG
| Total Weight of Lacing Weight in kg Shed - 1&2 |  |  |  |  | 784 | KG
h | Purlins with available material
Purlins 96x48x3.2mm
| 96x48x4.8mm | 10 | 50 |  |  | 500 | Rmt
[6 empty] | 550 | RMT
| Weight of Steel 6.71KG/Rmt | 1 | 550 | X | 6.71 | 3690.5
[5 empty] | Total | 4060 | KG
| Total Weight of Purlins Weight in kg Shed - 1 |  |  |  |  | 4060 | KG
Purlins with material
Purlins 96x48x4.8mm
| 96x48x4.8mm | 10 | 50 |  |  | 500 | Rmt
[6 empty] | 550 | RMT
| Weight of Steel 9.66KG/Rmt | 1 | 550 | X | 9.66 | 5313
[5 empty] | Total | 5844 | KG
| Total Weight of Purlins Weight in kg Shed - 2 |  |  |  |  | 5844 | KG
i | Tie Runners with material
Tie Runners 96x48x4.8mm
| 96x48x4.8mm | 8 | 50 |  |  | 400 | Rmt
[6 empty] | 440 | RMT
| Weight of Steel 9.66KG/Rmt | 1 | 440 | X | 9.66 | 4250.4
[5 empty] | Total | 4675 | KG
| Total Weight of Tie Runners Weight in kg Shed - 1&2 |  |  |  |  | 4675 | KG
| Grand Total Weight of provided Structural Steel for Shed-1&2 |  |  |  |  | 19572 | KG
| Grand Total Weight of fabrication Structural Steel for Shed-1&2 |  |  |  |  | 4060 | KG
PARKING SHED -3 (Both side Two Wheeler Parking)
1 | Galvanized Iron Sheet (G. I)
| Powder Coated G.I.Roof Sheet | 1 | 10.168 | 50.04 |  | 508.8067 | Sqm
[6 empty] | 509 | Sqm
B | Powder Coated G.I. Roof Sheet Qty. Shed -3 |  |  |  | Total | 559.9 | Sqm
2 | Structural Steel Works
a | ISMB - 200 | 20 | 3.6 |  |  | 72 | Rmt
[5 empty] | Total | 72 | Rmt
| ISMB -200- 25.4Rmt/Kg |  | 25.4 |  |  | 2012 | Kgs
b | Base Plate
Base Plate -250x300x16mm thick
| Base Plate 16mm Thick | 40 | 0.3 | 0.25 |  | 3 | Sqm
[5 empty] | Total | 3 | Sqm
| For 1SQM (251.2/2=125.60KG) |  | 125.6 |  |  | 414 | Kg
| Total Weight of Base Plate Weight in kg Shed -3 |  |  |  |  | 455.4 | KG
d | Card
Top Card 72x72x4.0mm
| Top Card 72x72x4.0mm | 10 | 10.168 |  |  | 101.68 | Rmt
[6 empty] | 111.848 | Rmt
| Weight of Steel 8.22KG/Rmt | 1 | 111.848 | X | 8.22 | 919.3906
[5 empty] | Total | 1011 | KG
Bottom Card 72x72x4.0mm
| Bottom Card 72x72x4.0mm | 10 | 10 |  |  | 100 | Rmt
[6 empty] | 110 | RMT
| Weight of Steel 8.22KG/Rmt | 1 | 110 | X | 8.22 | 904.2
[5 empty] | Total | 995 | KG
| Total Weight of Card Weight in kg Shed -3 |  |  |  |  | 2006 | KG
e | Web Members
Web Members 38x38x3.2mm
| 38x38x3.2mm | 10 | 10.944 |  |  | 109.44 | Rmt
[6 empty] | 120.384 | RMT
| Weight of Steel 3.29KG/Rmt | 1 | 120.384 | X | 3.29 | 396.0634
[5 empty] | Total | 436 | KG
| Total Weight of Web Members Weight in kg Shed - 3 |  |  |  |  | 436 | KG
f | Bracings
| SHS Bracings 25x25x3.2mm | 10 | 10.968 |  |  | 109.68 | Rmt
[6 empty] | 120.648 | RMT
| Weight of Steel 1.98KG/Rmt | 1 | 120.648 | X | 1.98 | 238.883
[5 empty] | Total | 263 | KG
| Total Weight of Bracing Weight in kg Shed - 3 |  |  |  |  | 263 | KG
g | Lacing
Lacing 50x25x3.2mm
| 50x25x3.2mm | 16 | 5 |  |  | 80 | Rmt
[6 empty] | 88 | RMT
| Weight of Steel 3.24KG/Rmt | 1 | 88 | X | 3.24 | 285.12
[5 empty] | Total | 314 | KG
| Total Weight of Lacing Weight in kg Shed - 3 |  |  |  |  | 314 | KG
h | Purlins
Purlins 122x61x4.5mm
| 122x61x4.5mm | 14 | 50 |  |  | 700 | Rmt
[6 empty] | 770 | RMT
| Weight of Steel 11.88KG/Rmt | 1 | 770 | X | 11.88 | 9147.6
[5 empty] | Total | 10062 | KG
| Total Weight of Purlins Weight in kg Shed - 3 |  |  |  |  | 10062 | KG
i | Tie Runners
Tie Runners 122x61x4.5mm
| 122x61x4.5mm | 5 | 50 |  |  | 250 | Rmt
[6 empty] | 275 | RMT
| Weight of Steel 11.88KG/Rmt | 1 | 275 | X | 11.88 | 3267
[5 empty] | Total | 3594 | KG
| Total Weight of Tie Runners Weight in kg Shed - 3 |  |  |  |  | 3594 | KG
| Grand Total Weight of provided Structural Steel for Shed-3 |  |  |  |  | 19142.4 | KG
1 | Roof sheeting
| Shed -1 &2 Grand Total G.I Powder Coated Roof Sheet Qty. |  |  |  |  | 561 | Sqm
| Shed - 3 Grand Total G.I Powder Coated Roof Sheet Qty. |  |  |  |  | 559.9 | Sqm
| Total area |  |  |  |  | 1120.9 | Sqm
2 | Providing & fabrication of Structural Steel
| Providing & fabrication of Structural Steel for Shed-1&2 |  |  |  |  | 19572 | Sqm
| Providing & fabrication of Structural Steel for Shed-3 |  |  |  |  | 19142.4 | Sqm
| Total Weight |  |  |  |  | 38714.4 | Sqm
3 | Fabrication of Structural Steel
| Fabrication of Structural Steel for Shed-1&2 |  |  |  |  | 4060 | Sqm
| Total Weight |  |  |  |  | 4060 | Sqm
3 | Gutter (600 mm over all girth)
| Gutter | 1 | 300 |  |  | 300 | Rmt
[6 empty] | 330 | RMT
4 | Rain water down take pipes
| 110mm Dia | 60 | 4.2 |  |  | 252 | Rmt
[5 empty] | Total | 252 | Rmt

## Ambulance Shed
PROPOSED CONSTRUCTION OF AMBULANCE SHED , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Ambulance Shed
1 | Site levelling | 1 | 20 | 5 |  | 100 | Sqm
[5 empty] | Total | 110 | Sqm
2 | Earth Work excavation
Under Footing For Stair Case
A) Upto 1.50 M
| F-1 | 2 | 1.5 | 1.5 | 1.5 | 6.75 | Cum
Under RR Masonry
| ALL Round Length | 1 | 12 | 0.53 | 1 | 6.36 | Cum
| Total |  |  |  |  | 14 | Cum
Above 1.50 till 3.00 M
| F-1 | 2 | 1.5 | 1.5 | 1.5 | 6.75 | Cum
| Total |  |  |  |  | 7 | Cum
| Total Quantity of Excavation |  |  |  |  | 21 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 21 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | -3 | Cum
| Sand Cohesion |  |  |  |  | -3 | Cum
| RCC Footing |  |  |  |  | -2 | Cum
| Below FFL Column |  |  |  |  | -1 | Cum
| Plinth Beam |  |  |  |  | 0 | Cum
| Below FFL RR Masonry |  |  |  |  | -8 | Cum
| Back fillingQty |  |  |  |  | 4 | Cum
| Basement Filling | 1 | 3.7 | 3 | 0.3 | 3.33 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | -14 | Cum
| Filling With Available Excavated Earth Considered | 100% | x | 21 |  | 21 | Cum
| Disposal of Excavated Earth |  |  |  |  | 0 | Cum
4 | PCC (1:4:8)
Under Footing
| F-1 | 2 | 1.5 | 1.5 | 0.1 | 0.45 | Cum
[5 empty] | Total | 0.495 | Cum
Under RR Masonry
| ALL Round Length | 1 | 12 | 0.6 | 0.1 | 0.72 | Cum
[5 empty] | Total | 0.792 | Cum
Under Room PCC
| Parking Shed Area | 1 | 4 | 3.2 | 0.1 | 1.28 | Cum
| Total |  |  |  | Total | 1.408 | Cum
| Total PCC quantity |  |  |  |  | 3 | Cum
5 | 230mm thick soling
Under Room
| Parking Shed Area | 1 | 3.5 | 3 | 0.23 | 2.415 | Cum
[5 empty] | Total | 3 | Cum
6 | ATT
| Anti terminate | 1 | 3.5 | 3 |  | 11 | Sqm
[6 empty] | 12 | Sqm
| TOTAL ATT Qty. |  |  |  |  | 12 | Sqm
7 | RR MASONRY
Under RR Masonry
Below NGL
| ALL Round Length | 1 | 12 | 0.45 | 0.9 | 4.86 | Cum
[6 empty] | 6 | Cum
Above NGL
| ALL Round Length | 1 | 12 | 0.38 | 0.3 | 1.368 | Cum
[6 empty] | 2 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 8 | Cum
8 | Plinth Protection
|  | 1 | 7.5 | 0.75 |  | 6 | Sqm
[6 empty] | 7 | Sqm
| Total Plinth Protection Qty. |  |  |  |  | 7 | Sqm
9 | R.C.C
a) | Under Footing
| F-1 | 2 | 1.2 | 1.2 | 0.5 | 1.44 | Cum
| Total footings RCC |  |  |  |  | 2 | Cum
b) | RCC Columns
GROUND FLOOR
Below FFL
| P1 | 2 | 0.3 | 0.3 | 2.32 | 0.4176 | Cum
| Total columns RCC (upto FFL) |  |  |  |  | 1 | Cum
| Columns |  | RCC (upto FFL) |  |  | 1 | Cum
c) | RCC plinth beams
| Ambulance Shed | 2 | 3 | 0.23 | 0.38 | 0.5244 | Cum
|  | 1 | 3.5 | 0.23 | 0.38 | 0.3059 | Cum
[6 empty] | 1 | Cum
| Plinth beam |  |  |  | TOTAL | 1 | Cum
RCC Concrete Work
| Total Rcc Qty. All Works Upto Plinth Level. |  |  |  |  | 4 | Cum
|  |  |  | Grand Total |  | 4 | Cum
10 | Supplying & Fabrication of Reinforcement steel
| Footings- 60 kg/cum |  | 2 | X | 60 | 120 | kg
| Plinth Beam- 150 kg/cum |  | 1 | X | 150 | 150 | kg
| Columns-250 kgs/cum |  | 1 | X | 250 | 250 | kg
| Roof beams-250 kgs/cum |  | 0 | X | 250 | 0 | kg
| Slabs-80 kgs/cum |  | 0 | X | 80 | 0 | kg
| Stair case-100 kgs/cum |  | 0 | X | 100 | 0 | kg
| Lintels etc., -80 kg/cum |  | 0 | X | 80 | 0 | kg
| Chajjas etc., -60 kg/cum |  | 0 | X | 60 | 0 | kg
|  |  | 4 |  |  | 520 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 26 | kg
[6 empty] | 546 | KG
[5 empty] | (or) | 1 | MT
11 | SHUTTERING
Under Footing
| F-1 | 2 | 4.8 |  | 0.5 | 4.8 | Sqm
| Total Foundation Shuttering |  |  |  |  | 5 | Sqm
RCC Columns
Below FFL
| P1 | 2 | 1.2 |  | 2.32 | 5.568 | Sqm
[6 empty] | 6 | Sqm
| Columns Shuttering |  | RCC (upto FFL) |  |  | 6 | Sqm
Shuttering For Plinth beams
| Ambulance Shed | 2 | 3 |  | 0.76 | 4.56 | Sqm
|  | 1 | 3.5 |  | 0.76 | 2.66 | Sqm
[6 empty] | 8 | Sqm
| Shuttering for Plinth beams |  |  |  |  | 8 | Sqm
VDF Shuttering
| Ambulance Shed | 1 | 13 |  | 0.15 | 1.95 | Sqm
[6 empty] | 2 | Sqm
12 | Brick Work
200mm Thick Brick Wall
| Ambulance Parking Shed Wall | 1 | 6.5 | 0.2 | 1 | 1.3 | Cum
| Total 200 mm brick work quantity |  |  |  |  | 2 | Cum
13 | Plastering
External plastering(20mm)
| Ambulance Parking Shed | 1 | 6.5 |  | 2.2 | 14.3 | Sqm
[5 empty] | Total | 16 | Sqm
| External plastering |  |  |  |  | 16 | Sqm
14 | Pointing on stone work
Above NGL
| All Round Length |  |  |  |  | 0 | Sqm
[6 empty] | 0 | Sqm
| Pointing Work |  |  |  | TOTAL | 0 | Sqm
15 | Painting
| External painting |  |  |  |  | 16 | Sqm
| Internal painting |  |  |  |  | 0 | Sqm
VDF Flooring
16 | Flooring
| Ambulance Shed | 1 | 3.5 | 3 | 0.15 | 1.575 | Cum
[6 empty] | 2 | Cum
17 | Cutting Grooves and filling with silicon waterproof sealant
| for every 3 m x 4m size area |  |  | - | - | 0 | RM
[5 empty] | Say | 0 | RM
18 | Laying of Hot top
| Solar Power Inverter | 1 | 3.5 | 3 |  | 10.5 | Sqm
[6 empty] | 12 | Sqm
19 | Fixing of Galvanized Iron Sheet (G. I) For Ambulance Shed
| Powder Coated G.I. Sheet Roof | 1 | 4 | 3.5 |  | 14 | Sqm
| Vertical Sheet | 1 | 6.5 |  | 2.6 | 16.9 | Sqm
[6 empty] | 31 | Sqm
[5 empty] | Total | 31 | Sqm
20 | Structural Steel Works
a) | Anchor Bolts
at FFL Lvl.
| 20mm Dia | 16 |  |  | 0.6 | 9.6 | Rmt
[6 empty] | 10.56 | RMT
| Weight of Steel 2.50KG/Rmt | 1 | 10.56 | X | 2.85 | 30.096
[5 empty] | Total | 30 | KG
For Details of @ '6' Anchored
| 16mm Dia | 16 |  |  | 0.35 | 5.6 | Rmt
[6 empty] | 6.16 | RMT
| Weight of Steel 1.60KG/Rmt | 1 | 6.16 | X | 1.6 | 9.856
[5 empty] | Total | 10 | KG
| Total Weight of Anchor Bolts Weight in kg |  |  |  |  | 40 | KG
b) | Base Plate
For Details of Base Plate
| Base Plate 20mm Thick | 16 | 0.3 | 0.3 |  | 1.44 | Sqm
[5 empty] | Total | 1.44 | Sqm
| For 1SQM (314.00/2=157KG) |  | 157 |  |  | 249 | Kg
For Details of @ '6' Anchored in Existing Column
For Details of Base Plate
| Base Plate 10mm Thick | 16 | 0.25 | 0.3 |  | 1.2 | Sqm
[5 empty] | Total | 1.2 | Sqm
| For 1SQM (157.00/2=78.50KG) |  | 78.5 |  |  | 104 | Kg
| Total Weight of Base Plate Weight in kg |  |  |  |  | 353 | KG
c) | CARD
Horizontal sides
Top Chord 60x60x4.0mm
| Top Chord 50x50x4.0mm | 4 | 3.5 |  |  | 14 | Rmt
[6 empty] | 15.4 | RMT
| Weight of Steel 5.44KG/Rmt | 1 | 15.4 | X | 5.44 | 83.776
[5 empty] | Total | 84 | KG
Bottom Chord 60x60x4.0mm
| Top Chord 50x50x4.0mm | 4 | 3.3 |  |  | 13.2 | Rmt
[6 empty] | 14.52 | RMT
| Weight of Steel 5.44KG/Rmt | 1 | 14.52 | X | 5.44 | 78.9888
[5 empty] | Total | 79 | KG
| Total Weight of Chord Weight in kg |  |  |  |  | 163 | KG
d) | Bracing
Horizontal sides
| SHS 25x25x3.2mm | 3 | 0.3 |  |  | 0.9 | Rmt
[6 empty] | 0.99 | RMT
| Weight of Steel 1.98KG/Rmt | 1 | 0.99 | X | 1.98 | 1.9602
[5 empty] | Total | 2 | KG
Vertical sides
| SHS 25x25x3.2mm | 3 | 1.2 |  |  | 3.6 | Rmt
[6 empty] | 3.96 | RMT
| Weight of Steel 1.98KG/Rmt | 1 | 3.96 | X | 1.98 | 7.8408
[5 empty] | Total | 8 | KG
| Total Weight of Bracing Weight in kg |  |  |  |  | 10 | KG
e) | Square Hallow Section Column
| Section - 100x100x5mm | 2 |  |  | 3 | 6 | Rmt
[6 empty] | 6.6 | RMT
| Weight of Steel 14.41KG/Rmt | 1 | 6.6 | X | 14.41 | 95.106
[5 empty] | Total | 95 | KG
| Total Weight of Square Section Column Weight in kg |  |  |  |  | 95 | KG
| Add : 10% Extra for Other Unforessen Items |  |  |  |  | 10 | kg
| Grand Total Weight of Structural Steel Work |  |  |  |  | 671 | KG
21 | Fabrication & fixing of structural steel
Square Hallow Section Purlin
| Section - 96x48x3.2mm | 4 |  |  | 4.5 | 18 | Rmt
[6 empty] | 18 | RMT
| Weight of Steel 6.71 KG/Rmt | 1 | 18 | X | 6.71 | 120.78
[5 empty] | Total | 121 | KG
| Total Weight of Square Section Column Weight in kg |  |  |  |  | 121 | KG
22 | Gutter (600 mm over all girth)
| Gutter | 1 | 3.5 |  |  | 3.5 | Rmt
[6 empty] | 4 | RMT
23 | Rain water down take pipes
| 110mm Dia | 2 | 3.8 |  |  | 7.6 | Rmt
[5 empty] | Total | 8 | Rmt

## Search Barrier Dtl
PROPOSED CONSTRUCTION OF SEARCH BARRIER, TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Search Barrier
1 | Site levelling | 0 | 6.48 | 10 |  | 0 | Sqm
[5 empty] | Total | 0 | Sqm
2 | Earth Work excavation
a) | Earth Work Excavation up to 1.50m
Under Footing
| F1 | 0 | 1.95 | 1.95 | 1.5 | 0 | Cum
| Total |  |  |  |  | 0 | Cum
b) | Earth Work Excavation 1.50m to 3.00m
Under Footing
| F1 | 0 | 1.95 | 1.95 | 1.2 | 0 | Cum
| Total |  |  |  |  | 0 | Cum
| Total Quantity of Excavation |  |  |  |  | 0 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 0 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | 0 | Cum
| Below FFL RR Masonry |  |  |  |  | 0 | Cum
| Back fillingQty |  |  |  |  | 0 | Cum
| Basement Filling | 0 | 4.48 | 8 | 0.3 | 0 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | 0 | Cum
| Filling With Available Excavated Earth Considered | 20% | x | 0 |  | 0 | Cum
| Disposal of Excavated Earth |  |  |  |  | 0 | Cum
4 | PCC (1:4:8)
Under Rcc Footing
| F1 | 0 | 1.95 | 1.95 | 0.1 | 0 | Cum
| Total |  |  |  | Total | 0 | Cum
Under CRS Masonry Wall
| For External Wall | 0 | 14.48 | 0.53 | 0.1 | 0 | Cum
| Total |  |  |  | Total | 0 | Cum
| Total PCC quantity |  |  |  |  | 0 | Cum
5 | RR MASONRY
Under RR Masonry
Below NGL
| For External Wall | 0 | 14.48 | 0.45 | 0.6 | 0 | Cum
[6 empty] | 0 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 0 | Cum
6 | RCC Footing
| F1 | 0 | 1.8 | 1.8 | 0.6 | 0 | Cum
[5 empty] | Total | 0 | Cum
| Total Footing Qty. |  |  |  |  | 0 | Cum
7 | RCC COLUMN
Below FFL
| P1 | 0 | 0.38 | 0.38 | 2 | 0 | Cum
[5 empty] | Total | 0 | Cum
| Total Pedstal Column Qty. |  |  |  |  | 0 | Cum
| a) All Works upto Plinth Level |  |  |  |  | 0 | Cum
| b) All Works above plinth and upto Floor V level |  |  |  |  | 0 | Cum
8 | Supplying & Fabrication of Reinforcement steel
| Footings- 60 kg/cum |  | 0 | X | 60 | 0 | kg
| Plinth Beam- 150 kg/cum |  | 0 | X | 150 | 0 | kg
| Columns-250 kgs/cum |  | 0 | X | 250 | 0 | kg
| Roof beams-250 kgs/cum |  | 0 | X | 250 | 0 | kg
| Slabs-80 kgs/cum |  | 0 | X | 80 | 0 | kg
| Stair case-100 kgs/cum |  | 0 | X | 100 | 0 | kg
| Lintels etc., -80 kg/cum |  | 0 | X | 80 | 0 | kg
| Chajjas etc., -60 kg/cum |  | 0 | X | 60 | 0 | kg
|  |  | 0 |  |  | 0 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 0 | kg
[6 empty] | 0 | KG
[5 empty] | (or) | 0 | MT
9 | SHUTTERING
RCC Footing
| F1 | 0 | 7.2 |  | 0.6 | 0 | Sqm
| Total Foundation Shuttering |  |  |  |  | 0 | Sqm
RCC COLUMN
Below FFL
| P1 | 0 | 1.52 |  | 2 | 0 | Sqm
[6 empty] | 0 | Sqm
10 | SS Railing
| Search Barrier | 0 | 4.48 | 8 |  | 0 | Sqm
|  |  |  | Grand Total |  | 0 | Sqm
| SS TUBES 18KGS /Sqm | 18 |  |  |  | 0 | KGS
8 | Galvanized Iron Sheet (G. I)
| Powder Coated G.I. Sheet Roof | 1 | 6 | 9 |  | 54 | Sqm
[6 empty] | 54 | Sqm
[5 empty] | Total | 54 | Sqm
9 | Structural Steel Works
Search Barrier
| For Roof Trusses | 1 | 6 | 9 |  | 54 | Sqm
[6 empty] | 59.4 | Sqm
| Converstion Weight of kg/sqm44Kg | 1 | 59.4 | X | 44 | 2613.6
[5 empty] | Total | 2614 | KG
| Add : 10% Extra for Other Unforessen Items |  |  |  |  | 261 | kg
| Total Weight of Structural Steel in kg |  |  |  |  | 2875 | KG
10 | Gutter (600 mm over all girth)
| Gutter | 1 | 15 |  |  | 15 | Rmt
[6 empty] | 17 | RMT
11 | Rain water down take pipes
| 110mm Dia | 4 | 3.95 |  |  | 15.8 | Rmt
[5 empty] | Total | 16 | Rmt

## Office Area-1 Toilet
PROPOSED CONSTRUCTION OF OFFICE AREA-1 TOILETS , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Toilet For SMD (Office -1)
1 | Site levelling |  |  |  |  | 0 | Sqm
[5 empty] | Total | 0 | Sqm
2 | Earth Work excavation
Under CSR Masonry For External Wall
| Horizontal Wall | [5 empty] | Cum
| Vertical Wall | [5 empty] | Cum
| Total |  |  |  |  | 0 | Cum
| Total Quantity of Excavation |  |  |  |  | 0 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 0 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) | [5 empty] | Cum
| Soling |  |  |  |  | 0 | Cum
| Below FFL RR Masonry |  |  |  |  | 0 | Cum
| Back fillingQty |  |  |  |  | 0 | Cum
| Basement Filling |  |  |  |  | 0 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | 0 | Cum
| Filling With Available Excavated Earth Considered | 0% | x | 0 |  | 0 | Cum
| Disposal of Excavated Earth |  |  |  |  | 0 | Cum
4 | PCC (1:4:8)
Under Toilet
| Under Room Area | 1 | 4.865 | 3 | 0.15 | 2.1892 | Cum
| Total |  |  |  | Total | 2.4082 | Cum
| Total PCC quantity |  |  |  |  | 2.4082 | Cum
5 | 230mm Thick Soling
Under Toilet
[6 empty] | 0 | Cum
[5 empty] | Total | 0 | Cum
6 | ATT
| Anti terminate |  |  |  |  | 0 | Sqm
[6 empty] | 0 | Sqm
| TOTAL ATT Qty. |  |  |  |  | 0 | Sqm
7 | RR MASONRY
Under RR Masonry
Below NGL
| Horizontal Wall |  |  |  |  | 0 | Cum
| Vertical Wall |  |  |  |  | 0 | Cum
[6 empty] | 0 | Cum
Above NGL
| Horizontal Wall |  |  |  |  | 0 | Cum
| Vertical Wall |  |  |  |  | 0 | Cum
[6 empty] | 0 | Cum
| TOTAL RR Masonry Qty. |  |  |  |  | 0 | Cum
8 | Plinth Protection
[6 empty] | 0 | Sqm
[6 empty] | 0 | Sqm
| Total Plinth Protection Qty. |  |  |  |  | 0 | Sqm
9 | Brick Work
CC-Block Brick Work
Ground Floor
| Horizontal Wall | 1 | 4.865 | 0.2 | 3.2 | 3.1136 | Cum
| Vertical Wall | 2 | 3 | 0.2 | 3.2 | 3.84 | Cum
Deduction
| D2 | 2 | 0.75 | 0.2 | 2.1 | -0.63 | Cum
| V | 2 | 0.6 | 0.2 | 0.45 | -0.108 | Cum
| Total 200mm brick work quantity |  |  |  |  | 7 | Cum
| 200mm Thick Brick Work |  | Ground Floor |  | TOTAL | 7 | Cum
10 | 100 mm Brick Wall
Half brick masonry
Ground Floor
Toilet in b/w Partion wall
| Horizontal Wall | 1 | 4.865 |  | 3.2 | 15.568 | Sqm
| Vertical Wall | 1 | 3 |  | 3.2 | 9.6 | Sqm
| Parapet Wall | 1 | 10.86 |  | 0.3 | 3.258 | Sqm
| Partion Wall | 2 | 0.75 |  | 2.1 | 3.15 | Sqm
Deduction
| D2 | 2 | 0.75 |  | 2.1 | -3.15 | Sqm
| Total 100 mm brick work quantity |  |  |  |  | 31 | Sqm
| 100 mm Brick Work |  | Ground Floor |  | TOTAL | 31 | Sqm
11 | Plastering
External plastering
| All round | 1 | 11 |  | 3.2 | 35.2 | Sqm
| Parapet Wall Plastering | 1 | 15.73 |  | 0.8 | 12.584 | Sqm
Deductions of 50% External
| D2 | 1 | 0.75 |  | 2.1 | -1.575 | Sqm
| V | 1 | 0.6 |  | 0.45 | -0.27 | Sqm
[5 empty] | Total | 51 | Sqm
| External plastering |  | Ground Floor |  |  | 51 | Sqm
12 | Internal plastering(15mm)
Ground Floor
| Toilet -M | 1 | 9.44 |  | 3.2 | 30.208 | Sqm
| WC | 1 | 5.17 |  | 3.2 | 16.544 | Sqm
| Toilet -F | 1 | 9.44 |  | 3.2 | 30.208 | Sqm
| WC | 1 | 5.17 |  | 3.2 | 16.544 | Sqm
| Partion Wall | 2 | 1.7 |  | 3.2 | 10.88 | Sqm
Deductions of 50% Internal
| D2 | 3 | 0.75 |  | 2.1 | -4.725 | Sqm
| V | 1 | 0.6 |  | 0.45 | -0.27 | Sqm
[5 empty] | Total | 109 | Sqm
| Internal plastering |  | Ground Floor |  | TOTAL | 109 | Sqm
13 | False Ceiling
| Toilet -M & F | 1 | 4.865 | 3 |  | 14.595 | Sqm
[6 empty] | 16 | Sqm
| False Ceiling |  | Ground Floor |  | TOTAL | 16 | Sqm
14 | Pointing on stone work
Above NGL
| Horizontal Wall | 0 | 0 |  | 0 | 0 | Sqm
| Vertical Wall | 0 | 0 |  | 0 | 0 | Sqm
[6 empty] | 0 | Sqm
| Pointing Work |  |  |  | TOTAL | 0 | Sqm
15 | Flooring
Non Skid Tiles Flooring
Ground Floor
| Toilet -M | 1 | 3.335 | 1.385 |  | 4.619 | Sqm
| WC | 1 | 1.2 | 1.385 |  | 1.662 | Sqm
| Toilet -F | 1 | 3.335 | 1.385 |  | 4.619 | Sqm
| WC | 1 | 1.2 | 1.385 |  | 1.662 | Sqm
[5 empty] | Total | 14 | Sqm
| Non Skid Tiles Flooring |  | Ground Floor |  | TOTAL | 14 | Sqm
16 | Dadoing
| Toilet -M | 1 | 9.44 |  | 3 | 28.32 | Sqm
| WC | 1 | 5.17 |  | 3 | 15.51 | Sqm
| Toilet -F | 1 | 9.44 |  | 3 | 28.32 | Sqm
| WC | 1 | 5.17 |  | 3 | 15.51 | Sqm
| Partion Wall | 2 | 1.5 |  | 3 | 9 | Sqm
[5 empty] | Total | 106 | Sqm
17 | Kota Stone Flooring
Ground Floor
Entrance Steps - 1
Sqm
Sqm
[5 empty] | Total | 0 | Sqm
| Kota Stone Flooring |  | Ground Floor |  | TOTAL | 0 | Sqm
18 | Painting
| External painting |  |  |  |  | 51 | Sqm
| Internal painting |  |  |  |  | 109 | Sqm
| Internal&External Paint With White Cement Based Putty |  |  |  |  | 160 | Sqm
19 | Water Proofing works
Toilet Water Proofing
| Toilet | 1 | 4.865 | 3 |  | 14.595 | Sqm
[5 empty] | Total | 16 | Sqm
20 | Joinery
Ground Floor
WPC Door Shutter 30mm Thick
| D2 | 4 | 0.75 |  | 2.1 | 6.3 | Sqm
[6 empty] | 6 | Sqm
| shutters |  |  |  | Total | 6 | Sqm
WPC Door Frames
| D2 | 4 | 4.95 |  |  | 19.8 | Rmt
[6 empty] | 20 | Rmt
21 | Ventilator Louvers
Ground Floor
| V | 2 | 1 |  | 0.45 | 0.9 | Sqm
[6 empty] | 1 | Sqm
| Ventilators |  |  |  | Total | 1 | Sqm
22 | Synthatic Enamel Paint
Wooden surface with approved primer
| D2 | 4 | 0.75 |  | 2.1 | 6.3 | Sqm
[5 empty] | Total | 7 | Sqm
23 | Galvanized Iron Sheet (G. I)
| Powder Coated G.I.Roof Sheet | 1 | 6.095 | 4.2 |  | 25.599 | Sqm
[6 empty] | 26 | Sqm
| Powder Coated G.I. Roof Sheet Qty. |  |  |  | Total | 26 | Sqm
24 | Fabrication & fixing of structural steel
Square Hallow Section Purlin
| Section - 96x48x3.2mm | 5 |  |  | 3.3 | 16.5 | Rmt
[6 empty] | 17 | RMT
| Weight of Steel 6.71 KG/Rmt | 1 | 17 | X | 6.71 | 114.07
[5 empty] | Total | 114 | KG
| Total Weight of Square Section Column Weight in kg |  |  |  |  | 114 | KG
25 | Gutter (600 mm over all girth)
| Gutter | 1 | 10.865 |  |  | 10.865 | Rmt
[6 empty] | 12 | RMT
SEWAGE
26 | European type
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty. |  |  |  |  | 2 | Nos
27 | Urinals
| Male Toilet | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
28 | Urinal Partitions
| Male Toilet | 2 |  |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
29 | Paper holder
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
30 | Health Faucet
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
31 | S.W. gully trap
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
32 | Gully chamber
|  | 1 | 2 |  |  | 2
| Total Qty |  |  |  |  | 2 | Nos
33 | P or S Trap
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
34 | Inspection Chamber
| IC 450 x 600 mm | 1 | 0 |  |  | 0
| Total Qty |  |  |  |  | 0 | Nos
35 | Manhole
| 500mm Dia Top and 1200mm Dia Bottom | 1 | 0 |  |  | 0
| Total Qty |  |  |  |  | 0 | Nos
36 | Soil Pipe
a) | 50mmØ SWR /PVC WASTE Water PIPE | 1 | 12 |  |  | 12 | Rmt
[6 empty] | 12 | Rmt
b) | 75mmØ SWR /PVC WASTE Water PIPE | 1 | 25 |  |  | 25 | Rmt
[6 empty] | 25 | Rmt
c) | 75mmØ SWR /PVC WASTE Water PIPE&Vent
|  | 1 | 2 |  |  | 2
[6 empty] | 2 | Nos
d) | 110mmØ SWR /PVC SOIL WASTE PIPE | 1 | 20 |  |  | 20 | Rmt
[6 empty] | 20 | Rmt
e) | 110mmØ SWR /PVC WASTE Water PIPE&Vent
|  | 1 | 2 |  |  | 2
[6 empty] | 2 | Nos
f) | 150mmØ SWR /PVC SOIL WASTE PIPE | 1 | 0 |  |  | 0 | Rmt
[6 empty] | 0 | Rmt
37 | Rain water down take pipes
| 110mm Dia | 1 | 5 |  |  | 5 | Rmt
[5 empty] | Total | 5 | Rmt
WATER SUPPLY
38 | WASH BASINS
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
39 | Bottle Trap
| Male Toilet | 1 | 3 |  |  | 3 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 4 | Nos
40 | Floor Trap
| Male Toilet | 1 | 2 |  |  | 2 | Nos
| Female Toilet | 1 | 2 |  |  | 2 | Nos
| Total Qty |  |  |  |  | 4 | Nos
41 | Two Way Bib Cock
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
42 | Long Body Bib Cock
| Male Toilet | 1 | 0 |  |  | 0 | Nos
| Female Toilet | 1 | 0 |  |  | 0 | Nos
| Total Qty |  |  |  |  | 0 | Nos
43 | Stop Cock
| Male Toilet | 1 | 2 |  |  | 2 | Nos
| Female Toilet | 1 | 0 |  |  | 0 | Nos
| Total Qty |  |  |  |  | 2 | Nos
44 | Mirror Glass
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
45 | Towel Ring
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
46 | Soap Dish
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
47 | Double Towel Bar
| Male Toilet | 1 | 0 |  |  | 0 | Nos
| Female Toilet | 1 | 0 |  |  | 0 | Nos
| Total Qty |  |  |  |  | 0 | Nos
48 | Robe Hook
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
49 | Angle Valve
| Male Toilet | 1 | 3 |  |  | 3 | Nos
| Female Toilet | 1 | 3 |  |  | 3 | Nos
| Total Qty |  |  |  |  | 6 | Nos
50 | Stain Less Steel Bib Cock
| Male Toilet | 1 | 1 |  |  | 1 | Nos
| Female Toilet | 1 | 1 |  |  | 1 | Nos
| Total Qty |  |  |  |  | 2 | Nos
51 | 15mmØ CPVC Line | 1 | 0 |  |  | 0 | Rmt
[6 empty] | 0 | Rmt
52 | 20mmØ CPVC Line | 1 | 0 |  |  | 0 | Rmt
[6 empty] | 0 | Rmt
53 | 25mmØ CPVC Line | 1 | 28 |  |  | 28 | Rmt
[6 empty] | 28 | Rmt
54 | 32mmØ CPVC Line | 1 | 0 |  |  | 0 | Rmt
[6 empty] | 0 | Rmt
55 | 32mmØ CPVC Down Take Pipe | 1 | 5.2 |  |  | 5.2 | Rmt
[6 empty] | 5 | Rmt
56 | 25mmØ CPVC UP Take Pipe | 1 | 4.2 |  |  | 4.2 | Rmt
[6 empty] | 4 | Rmt
[5 empty] | Total | 32 | Rmt
57 | Gate Valve
| 25mm dia | 1 | 1 |  |  | 1
| 32mm dia | 1 | 1 |  |  | 1
[6 empty] | 2 | Nos
58 | Rain water down take pipes
| 110mm Dia | 1 | 5 |  |  | 5 | Rmt
[5 empty] | Total | 5 | Rmt

## Approach roads
PROPOSED CONSTRUCTION OF APPROACH ROADS , TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Detailed Estimation of Approach Roads
1 | Site levelling
| Workers Rest Room & Change Room | 2 | 2.5 | 3 |  | 15 | Sqm
| Central Excise office | 1 | 2.5 | 3 |  | 7.5 | Sqm
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3 |  | 36.045 | Sqm
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3 |  | 173.646 | Sqm
| Helath Care Center | 1 | 5.5 | 3 |  | 16.5 | Sqm
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  |  | 107.93 | Sqm
| Parking Shed | 1 | 8.591 | 3 |  | 25.773 | Sqm
| Oil Store | 2 | 3.5 | 3 |  | 21 | Sqm
| Security Extension Room | 1 | 8 | 3 |  | 24 | Sqm
| Toilet Blocks | 1 | 11.55 | 3 |  | 34.65 | Sqm
[5 empty] | Total | 509 | Sqm
2 | Earth Work excavation
Under CSR Masonry For External Wall
| Workers Rest Room & Change Room | 2 | 2.5 | 3 | 1 | 15 | Cum
| Central Excise office | 1 | 2.5 | 3 | 1 | 7.5 | Cum
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3 | 1 | 36.045 | Cum
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3 | 1 | 173.646 | Cum
| Helath Care Center | 1 | 5.5 | 3 | 1 | 16.5 | Cum
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  | 0.9 | 97.137 | Cum
| Parking Shed | 1 | 8.591 | 3 | 1 | 25.773 | Cum
| Oil Store | 2 | 3.5 | 3 | 1 | 21 | Cum
| Security Extension Room | 1 | 8 | 3 | 1 | 24 | Cum
| Toilet Blocks | 1 | 11.55 | 3 | 1 | 34.65 | Cum
| Total |  |  |  |  | 496 | Cum
| Total Quantity of Excavation |  |  |  |  | 496 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 496 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | -51 | Cum
| Soling 230mm Thick |  |  |  |  | -117 | Cum
| Murum Filling |  |  |  |  | -152 | Cum
| 150mm Thick CC Road Laying |  |  |  |  | -80 | Cum
| Back fillingQty |  |  |  |  | 96 | Cum
| Filling With Available Excavated Earth Considered | 0% | x | 496 |  | 96 | Cum
| Disposal of Excavated Earth |  |  |  |  | 400 | Cum
4 | Murum Filling Brought from out side
| Workers Rest Room & Change Room | 2 | 2.5 | 3 | 0.3 | 4.5 | Cum
| Central Excise office | 1 | 2.5 | 3 | 0.3 | 2.25 | Cum
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3 | 0.3 | 10.8135 | Cum
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3 | 0.3 | 52.0938 | Cum
| Helath Care Center | 1 | 5.5 | 3 | 0.3 | 4.95 | Cum
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  | 0.3 | 32.379 | Cum
| Parking Shed | 1 | 8.591 | 3 | 0.3 | 7.7319 | Cum
| Oil Store | 2 | 3.5 | 3 | 0.3 | 6.3 | Cum
| Security Extension Room | 1 | 8 | 3 | 0.3 | 7.2 | Cum
| Toilet Blocks | 1 | 11.55 | 3 | 0.3 | 10.395 | Cum
[5 empty] | Total | 152 | Cum
5 | Preparation of Sub-Grade
| Workers Rest Room & Change Room | 2 | 2.5 | 3 |  | 15 | Sqm
| Central Excise office | 1 | 2.5 | 3 |  | 7.5 | Sqm
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3 |  | 36.045 | Sqm
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3 |  | 173.646 | Sqm
| Helath Care Center | 1 | 5.5 | 3 |  | 16.5 | Sqm
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  |  | 107.93 | Sqm
| Parking Shed | 1 | 8.591 | 3 |  | 25.773 | Sqm
| Oil Store | 2 | 3.5 | 3 |  | 21 | Sqm
| Security Extension Room | 1 | 8 | 3 |  | 24 | Sqm
| Toilet Blocks | 1 | 11.55 | 3 |  | 34.65 | Sqm
[5 empty] | Total | 508 | Sqm
6 | 230mm Thick Soling
Under Toilet
| Workers Rest Room & Change Room | 2 | 2.5 | 3 | 0.23 | 3.45 | Cum
| Central Excise office | 1 | 2.5 | 3 | 0.23 | 1.725 | Cum
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3 | 0.23 | 8.2904 | Cum
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3 | 0.23 | 39.9386 | Cum
| Helath Care Center | 1 | 5.5 | 3 | 0.23 | 3.795 | Cum
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  | 0.23 | 24.8239 | Cum
| Parking Shed | 1 | 8.591 | 3 | 0.23 | 5.9278 | Cum
| Oil Store | 2 | 3.5 | 3 | 0.23 | 4.83 | Cum
| Security Extension Room | 1 | 8 | 3 | 0.23 | 5.52 | Cum
| Toilet Blocks | 1 | 11.55 | 3 | 0.23 | 7.9695 | Cum
[5 empty] | Total | 117 | Cum
7 | PCC (1:4:8)
| Workers Rest Room & Change Room | 2 | 2.5 | 3 | 0.1 | 1.5 | Cum
| Central Excise office | 1 | 2.5 | 3 | 0.1 | 0.75 | Cum
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3 | 0.1 | 3.6045 | Cum
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3 | 0.1 | 17.3646 | Cum
| Helath Care Center | 1 | 5.5 | 3 | 0.1 | 1.65 | Cum
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  | 0.1 | 10.793 | Cum
| Parking Shed | 1 | 8.591 | 3 | 0.1 | 2.5773 | Cum
| Oil Store | 2 | 3.5 | 3 | 0.1 | 2.1 | Cum
| Security Extension Room | 1 | 8 | 3 | 0.1 | 2.4 | Cum
| Toilet Blocks | 1 | 11.55 | 3 | 0.1 | 3.465 | Cum
[5 empty] | Total | 50.8248 | Cum
| Total PCC quantity |  |  |  |  | 51 | Cum
8 | 150mm Thick CC ROAD
| Workers Rest Room & Change Room | 2 | 2.5 | 3 | 0.15 | 2.25 | Cum
| Central Excise office | 1 | 2.5 | 3 | 0.15 | 1.125 | Cum
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3 | 0.15 | 5.4067 | Cum
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3 | 0.15 | 26.0469 | Cum
| Helath Care Center | 1 | 5.5 | 3 | 0.15 | 2.475 | Cum
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  | 0.15 | 16.1895 | Cum
| Parking Shed | 1 | 8.591 | 3 | 0.15 | 3.8659 | Cum
| Oil Store | 2 | 3.5 | 3 | 0.15 | 3.15 | Cum
| Security Extension Room | 1 | 8 | 3 | 0.15 | 3.6 | Cum
| Toilet Blocks | 1 | 11.55 | 3 | 0.15 | 5.1975 | Cum
[5 empty] | Total | 79.7026 | Cum
| Total CC Road Qty. |  |  |  |  | 80 | Cum
9 | Supplying & Fabrication of Reinforcement steel
| Description | DIA in mm | Nos | No.of Rods | Length in Mt | Total Length in Mt | 10 dia
| Workers Rest Room & Change Room | 2 | 2.5 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 2 | 14 | 2.96 | 82.88 | 82.88
| Vertical Sides Bars &200mm c/c | 10 | 2 | 16 | 2.46 | 78.72 | 78.72
| Central Excise office | 1 | 2.5 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 14 | 2.96 | 41.44 | 41.44
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 2.46 | 39.36 | 39.36
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 62 | 2.96 | 183.52 | 183.52
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 11.975 | 191.6 | 191.6
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 265 | 3.26 | 863.9 | 863.9
| Vertical Sides Bars &200mm c/c | 10 | 1 | 18 | 52.58 | 946.44 | 946.44
| Helath Care Center | 1 | 5.5 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 29 | 2.96 | 85.84 | 85.84
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 5.46 | 87.36 | 87.36
| Ambulance Shed Front & Balnce Besie Area | 1 | 18.298 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 93 | 2.96 | 275.28 | 275.28
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 18.258 | 292.13 | 292.128
| Ambulance Shed Front & Balnce Besie Area | 1 | 10.098 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 52 | 2.96 | 153.92 | 153.92
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 10.058 | 160.93 | 160.928
| Ambulance Shed Front & Balnce Besie Area | 1 | 3.3 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 18 | 2.96 | 53.28 | 53.28
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 3.26 | 52.16 | 52.16
| Ambulance Shed Front & Balnce Besie Area | 1 | 5.95 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 31 | 2.96 | 91.76 | 91.76
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 5.91 | 94.56 | 94.56
| Parking Shed | 1 | 8.591 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 44 | 2.96 | 130.24 | 130.24
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 8.551 | 136.82 | 136.816
| Oil Store | 2 | 3.5 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 2 | 19 | 2.96 | 112.48 | 112.48
| Vertical Sides Bars &200mm c/c | 10 | 2 | 16 | 3.46 | 110.72 | 110.72
| Security Extension Room | 1 | 8 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 41 | 2.96 | 121.36 | 121.36
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 7.96 | 127.36 | 127.36
| Toilet Blocks | 1 | 11.55 | 3
| Horizontal Sides Bars 200mm c/c | 10 | 1 | 59 | 2.96 | 174.64 | 174.64
| Vertical Sides Bars &200mm c/c | 10 | 1 | 16 | 11.51 | 184.16 | 184.16
| Total Steel Qty in Rmt | [5 empty] | 5360.1372
| Unit weight in Kg /m | [5 empty] | 0.61652
| Weigth of Steel In kg | [5 empty] | 3304.65
| Grand Total Weight of Steel In kgs | [5 empty] | 3305
10 | Form Work For Roads Sides Shuttering
| Workers Rest Room & Change Room | 4 | 2.5 |  | 0.15 | 1.5 | Sqm
| Central Excise office | 2 | 2.5 |  | 0.15 | 0.75 | Sqm
| Contractor Toilet & Rest Room Road -1 | 2 | 12.015 |  | 0.15 | 3.6045 | Sqm
| Contractor Toilet & Rest Room Road -2 | 2 | 52.62 |  | 0.15 | 15.786 | Sqm
| Helath Care Center | 2 | 5.5 |  | 0.15 | 1.65 | Sqm
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  | 0.15 | 16.1895 | Sqm
| Parking Shed | 2 | 8.591 |  | 0.15 | 2.5773 | Sqm
| Oil Store | 4 | 3.5 |  | 0.15 | 2.1 | Sqm
| Security Extension Room | 2 | 8 |  | 0.15 | 2.4 | Sqm
| Toilet Blocks | 2 | 11.55 |  | 0.15 | 3.465 | Sqm
[5 empty] | Total | 55.0245 | Sqm
| Total CC Roads Sides Shuttering |  |  |  |  | 56 | Sqm
11 | Roads Groove Cutting
| Workers Rest Room & Change Room | 2 | 2.5 | 3 |  | 15 | Sqm
| Central Excise office | 1 | 2.5 | 3 |  | 7.5 | Sqm
| Contractor Toilet & Rest Room Road -1 | 1 | 12.015 | 3 |  | 36.045 | Sqm
| Contractor Toilet & Rest Room Road -2 | 1 | 52.62 | 3.3 |  | 173.646 | Sqm
| Helath Care Center | 1 | 5.5 | 3 |  | 16.5 | Sqm
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  |  | 107.93 | Sqm
| Parking Shed | 1 | 8.591 | 3 |  | 25.773 | Sqm
| Oil Store | 2 | 3.5 | 3 |  | 21 | Sqm
| Security Extension Room | 1 | 8 | 3 |  | 24 | Sqm
| Toilet Blocks | 1 | 11.55 | 3 |  | 34.65 | Sqm
[5 empty] | Total | 508.2484 | Sqm
| Total CC Roads Grooves Cutting |  |  |  |  | 509 | Sqm
12 | Kerb Stone of M25 Grade Cement Concrete
| Workers Rest Room & Change Room | 4 | 2.5 | 0.125 | 0.6 | 0.75 | Cum
| Central Excise office | 2 | 2.5 | 0.125 | 0.6 | 0.375 | Cum
| Contractor Toilet & Rest Room Road -1 | 2 | 12.015 | 0.125 | 0.6 | 1.8022 | Cum
| Contractor Toilet & Rest Room Road -2 | 2 | 52.62 | 0.125 | 0.6 | 7.893 | Cum
| Helath Care Center | 2 | 5.5 | 0.125 | 0.6 | 0.825 | Cum
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 | 0.125 | 0.6 | 8.0947 | Cum
| Parking Shed | 2 | 8.591 | 0.125 | 0.6 | 1.2886 | Cum
| Oil Store | 4 | 3.5 | 0.125 | 0.6 | 1.05 | Cum
| Security Extension Room | 2 | 8 | 0.125 | 0.6 | 1.2 | Cum
| Toilet Blocks | 2 | 11.55 | 0.125 | 0.6 | 1.7325 | Cum
[5 empty] | Total | 27.5123 | Cum
| Total Kerb Stone QTY. |  |  |  |  | 28 | Cum
13 | Painting road surface
| Workers Rest Room & Change Room | 4 | 2.5 |  | 0.6 | 6 | Sqm
| Central Excise office | 2 | 2.5 |  | 0.6 | 3 | Sqm
| Contractor Toilet & Rest Room Road -1 | 2 | 12.015 |  | 0.6 | 14.418 | Sqm
| Contractor Toilet & Rest Room Road -2 | 2 | 52.62 |  | 0.6 | 63.144 | Sqm
| Helath Care Center | 2 | 5.5 |  | 0.6 | 6.6 | Sqm
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 |  | 0.6 | 64.758 | Sqm
| Parking Shed | 2 | 8.591 |  | 0.6 | 10.3092 | Sqm
| Oil Store | 4 | 3.5 |  | 0.6 | 8.4 | Sqm
| Security Extension Room | 2 | 8 |  | 0.6 | 9.6 | Sqm
| Toilet Blocks | 2 | 11.55 |  | 0.6 | 13.86 | Sqm
[5 empty] | Total | 220.0981 | Sqm
| Total Painting on Road Surface Qty. |  |  |  |  | 221 | Sqm
14 | Non-pressure NP2 class (light duty) R.C.C. pipes
| 150mm Dia | 1 | 50 |  |  | 50 | Rmt
| 250mm Dia | 1 | 50 |  |  | 50 | Rmt
| 300mm Dia | 1 | 200 |  |  | 200 | Rmt
[5 empty] | Total | 330 | Rmt
| Total Non- Pressure NP2 Class Qty. |  |  |  |  | 330 | Rmt
15 | Kerb Channel 150cm Wide ( Saucer Darin)
| Workers Rest Room & Change Room | 4 | 2.5 | 0.15 |  | 1.5 | Sqm
| Central Excise office | 2 | 2.5 | 0.15 |  | 0.75 | Sqm
| Contractor Toilet & Rest Room Road -1 | 2 | 12.015 | 0.15 |  | 3.6045 | Sqm
| Contractor Toilet & Rest Room Road -2 | 2 | 52.62 | 0.15 |  | 15.786 | Sqm
| Helath Care Center | 2 | 5.5 | 0.15 |  | 1.65 | Sqm
| Ambulance Shed Front & Balnce Besie Area | 1 | 107.93 | 0.15 |  | 16.1895 | Sqm
| Parking Shed | 2 | 8.591 | 0.15 |  | 2.5773 | Sqm
| Oil Store | 4 | 3.5 | 0.15 |  | 2.1 | Sqm
| Security Extension Room | 2 | 8 | 0.15 |  | 2.4 | Sqm
| Toilet Blocks | 2 | 11.55 | 0.15 |  | 3.465 | Sqm
[5 empty] | Total | 55.0245 | Sqm
| Total Kerb Channel Qty. |  |  |  |  | 56 | Sqm

## SEPTIC TANK(100 CAPACITY)
VELLORE INSTITUTE OF TECHNOLOGY AT CHENNAI CAMPUS.
VST INDUSTRIES PVT LTD
CONSTRUCTION OF SEPTIC TANK FOR 150 CAPACITY
CIVIL WORKS DETAILS
S.NO | DESCRIPTION OF ITEMS | NOS | LENGTH | BREADTH | DEPTH | QUANTITY
1 | clearing jungle including uprooting of rank vegetation, grass, brush wood, trees and saplings of girth up to 30 cm measured at a height of 1 m above ground level and removal of rubbish up to a distance of 50 m outside the periphery of the area cleared
Site claerance
|  | 1 | 20 | 10 |  | 200
3 | General Excavation by mechanical means in all types of soil including dense soil, discentegrated/ weathered/ soft rock including necessary manual excavation for dressing the edges & leveling, all leads and lifts back filling in layers of 150mm with watered compaction. Rate to include disposing the excess earth and spreading in layers to the required levels within the site wherever specified. and disposing of surplus earth / excavated material out side the plot and disposing of the same to the designrated areas identified by the local Authorities . contractor has to make necessary enquiry and made his arrangements as his own for disposing of excess earth, dewatering of both ground and surface water, removal of slurry generated while excavation and keeping the area free of water with necessary shoring, strutting required for keeping earth in position etc,. excavating loose pockets and compacting the same. Note:Authorised working space and Provision of slopes if required for execution shall not be paid separately. Excavation in all types of soils to any depth below natural ground level.
Earthwork excavation
|  | 1 | 8.9 | 4.05 | 1.5 | 54
|  | 1 | 8.9 | 4.05 | 1 | 36
90
4 | Providing and laying plain cement concrete 1:4:8(1: cement 4: coarse sand 8: graded stone aggregate 40mm nominal size ) using H. B. G(Hard borken granite) coarse graded aggregate of 40 mm and down size for levelling course under footings, steps, walls, platform etc., including laying layers of specified thickness in alternative bays not exceeding 10 sqm as directed including form work wherever necessary and well compacted etc., all complete, as directed by Engineer-in-charge/Architect.(Grade of Mix 7.5)
| CC (1:4:8) | 1 | 8.9 | 4.05 | 0.1 | 4
4
5 | providing and laying in position ready mixed or site batched design mix Cement concrete for reinforced cement concrete work; using coarse aggregate and fine aggregate derived from natural sources, portland pozzolana / ordinary portland /portland Slag cement, admixtures in recommended proportions as per iS: 9103 to accelerate / retard setting of concrete, to improve durability and workability without impairing strength; including pumping of concrete to site of laying, curing, carriage for all leads; but excluding the cost of centering, shuttering,finishing and reinforcement as per direction of the engineer-in-charge; for the following grades of concrete. Note: Extra cement up to 10% of the minimum specified cement content in design mix shall be payable separately. in case the cement content in design mix is more than 110% of the specified minimum cement content, the contractor shall have discretion to either re-design the mix or bear the cost of extra cement. 5.33.1 All works upto plinth level M25 GRADE OF CONCRETE
A | RCC BOT SLAB 230MM THICK | 1 | 8.2 | 3.05 | 0.23 | 6
B | RCC WALLS 200mm thick
|  | 2 | 7.9 | 0.2 | 1.9 | 6
|  | 1 | 2.65 | 0.2 | 1.5 | 1
|  | 1 | 2.65 | 0.2 | 2.3 | 1
| RCC PARTITION | 1 | 2.65 | 0.2 | 1.5 | 1
9
C | RCC TOP SLAB 115MM THICK | 1 | 7.9 | 3.05 | 0.125 | 3
18
6 | Providing, fabricating and erecting of steel form work at all levels and places wherever needed/ specified as per drawing including striking with not less than 12mm Plastic coated, marine resistant water proof ply/ smooth finished MS plates with adjustable steel props of acceptable staging system and with sufficient bracing as approved by consultant. Cost to include designing of proper form work and staging system to suit the requirements, Submission of design calculations and shop drawings for approval, sealing the joints with heavy duty brown self adhesive tape, aligning to line and levels including M.S. Ties (including grouting), PVC Spacer/Precast cover blocks, Providing openings/ cutouts/ pockets, deshuttering, applying chemical for shuttering as approved by the consultant etc., complete at all levels
| rcc bot slab sides | 1 | 22.5 |  | 0.23 | 5
| rcc walls | 4 | 7.9 |  | 1.9 | 60
|  | 2 | 2.65 |  | 1.5 | 8
|  | 4 | 2.65 |  | 2.3 | 24
| PARTITION WALL | 2 | 2.65 |  | 1.5 | 8
100
| rcc top slab | 1 | 7.9 | 3.05 |  | 24
7 | Providing and fixing reinforcement for RCC work with high yield strength ribbed tor steel (HYSD) bar of various diameters and grade of steel as specified below conforming to IS or equivalent BS specification including cutting and waste, bending, hoisting, fabricating and placing in position according to drawings and binding the reinforcement with galvanised annealed binding wire of double fold of 18 gauge and providing PVC cover blocks for placing the reinforcements in position and for maintaining the cover specified and/or according to relevant IS or equivalent BS code. (The rate include all wastages and rolling margines) complete .
HSYD STEEL BARS
| RCC BOT SLAB 230MM THICK |  | 6 | 100 |  | 600
| RCC WALLS 200mm thick |  | 9 | 250 |  | 2250
| RCC TOP SLAB 115MM THICK |  | 3 | 80 |  | 240
| WASTAGE @15% |  |  |  |  | 463.5
3909
8 | 62 mm thick cement concrete flooring with concrete hardener topping, under layer 50mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) and top layer 12mm thick cement hardener consisting of mix 1:2 (1 cement hardener mix : 2 graded stone aggregate, 6mm nominal size) by volume, hardening compound mixed @ 2 litre per 50 kg of cement or as per manufacture’s specifications. This includes cost of cement slurry, but excluding the cost of nosing of steps etc. complete
|  | 1 | 7.8 | 2.65 |  | 30
9 | 6 mm cement plaster 1:3 (1 cement : 3 fine sand) finished with a floating coat of neat cement and thick coat of Lime wash on top of walls when dry for bearing of R.C.C. slabs and beams.
| ceiling plastering | 1 | 7.9 | 2.65 |  | 21
21
10 | Providing & laying 18 mm thick cement Plaster to Internal walls columns, piers etc. in cement mortar 1 : 4 (1 cement : 4 sand; 75% fine sand & 25% coarse sand) on plain side of wall or R.C.C. surface including fixing 150 mm Wide Plaster mesh made out of galvanized iron of nominal thickness 0.35 mm at the junctions of Masonry and concrete works, chasing Works 200 mm Width, Diagonal fixing at Doors & Windows Opening to a width of 300 mm x 600 mm; Corner Bead of size 45 x 45 mm made out of galvanized iron of nominal thickness 0.45 mm with a Zinc coating of 120 gms per Sqm as protector for plastered wall and column corners/edges from chipping, including tying in position by using suitable nails / clamps / screws including tying in position with suitable nails / screws etc., complete and as per manufacturer specification of approved make. Rate shall include for preparation of surface, cleaning, curing, scaffolding hacking, labour materials etc. complete for all levels and heights as directed.
| Internal Plastering 18mm thick | 2 | 7.5 |  | 1.9 | 29
|  | 1 | 2.65 |  | 1.5 | 4
|  | 1 | 2.65 |  | 2.3 | 6
|  | 2 | 2.65 |  | 1.5 | 8
47
11 | Providing and laying integral cement based treatment for water proofing on horizontal surface at all depth below ground level for under ground structures as directed by Engineer-in-Charge and consisting of : (i) Ist layer of 22 mm to 25 mm thick approved and specified rough stone slab over a 25 mm thick base of cement mortar 1:3 (1 cement : 3 coarse sand) including applying of twice ( at base and top of mortar ) cement slurry @ 2.2kg/m2 (each time) mixed with water proofing compound conforming to IS:2645 in the recommended proportion over the leveling course (leveling course to be paid separately). Joints sealed and grouted with cement slurry mixed with water proofing compound. (ii) 2nd layer of 25 mm thick cement mortar 1:3 (1 cement: 3 coarse sand) mixed with water proofing compound in recommended proportions. (iii) Finishing top with stone aggregate of 10 mm to 12 mm nominal size spreading @ 8 cudm/ sqm thoroughly embedded in the 2nd layer including smooth plastering of 12mm thick complete for finished item of work.
External waterproofing
|  | 2 | 7.9 |  | 2.5 | 40
|  | 1 | 3.05 |  | 2.9 | 9
|  | 1 | 3.05 |  | 2.1 | 6
55
12 | Providing, fixing, testing and commissioning of 110 mm pipe diameter uPVC SWR Type B pipe comforming to IS : 13592, including jointing with seal ring conforming to IS : 5382 for vertical pipe & Selfit uPVC Adhesive solvent joint inside in the toilet, including all fittings such as bends, junctions, inspection doors, offests, cowl, clean out, access pieces/plugs etc. complete the job. The rate shall be including all the engineered support at every one Meter (support, hanger, nuts/ bolts, anchor fasteners, fixing clamp/channels with U-bolts, etc) as per detail technical specification etc. complete the job.
| PVC 4" INLET AND VENT PIPE | 1 | 15 |  |  | 15
13 | Providing, fixing, testing and commissioning of 150 mm pipe diameter uPVC SWR Type B pipe comforming to IS : 13592, including jointing with seal ring conforming to IS : 5382 for vertical pipe & Selfit uPVC Adhesive solvent joint inside in the toilet, including all fittings such as bends, junctions, inspection doors, offests, cowl, clean out, access pieces/plugs etc. complete the job. The rate shall be including all the engineered support at every one Meter (support, hanger, nuts/ bolts, anchor fasteners, fixing clamp/channels with U-bolts, etc) as per detail technical specification etc. complete the job.
| PVC 6" OUTLET PIPE | 1 | 10 |  |  | 10
14 | M.H cover 600mmx600mm | 2 |  |  |  | 2
15 | Encapsuled PVC steps | 12 |  |  |  | 12
GRAND TOTAL AMOUNT

## Sump & External Servieces Dtl
PROPOSED CONSTRUCTION OF PROPOSED SUMP, TOOPRAN -HYDERABAD , TELANGANA - 500020.
S.NO | DESCRIPTION | NOS | LENGTH | BREDTH | DEPTH | QUANTITY | UNITS
Sump For R&D
1 | Site levelling | 1 | 7.1 | 7.1 |  | 50.41 | Sqm
Collection Sump
| Site levelling | 1 | 7.1 | 7.1 |  | 50.41 | Sqm
[5 empty] | Total | 111 | Sqm
2 | Earth Work excavation
Under Footing For Stair Case
Sump For R&D and Collection Sump
A) Upto 1.50 M
| Sump | 2 | 2.65 | 2.65 | 1.5 | 21.0675 | Cum
| Total |  |  |  |  | 23 | Cum
Above 1.50 till 3.00 M
| Sump | 2 | 2.65 | 2.65 | 0.275 | 3.8624 | Cum
| Total |  |  |  |  | 4 | Cum
| Total Quantity of Excavation |  |  |  |  | 27 | Cum
3 | Supply & Filling Earth in sides of Footings, Under Basements etc.,
| Available Excavated Earth Quantity |  |  |  |  | 27 | Cum
Deduct Quantities of
| Deduction PCC (1:4:8) |  |  |  |  | -2 | Cum
| RCC Footing |  |  |  |  | -3 | Cum
| Below FFL Column |  |  |  |  | -5 | Cum
| Sump Slab |  |  |  |  | -2 | Cum
| Back fillingQty |  |  |  |  | 15 | Cum
| Supply & Filling of Good Earth Brought From Out Side |  |  |  |  | 15 | Cum
| Filling With Available Excavated Earth Considered | 0% | x | 27 |  | 0 | Cum
| Disposal of Excavated Earth |  |  |  |  | 27 | Cum
4 | PCC (1:4:8)
Sump For R&D and Collection Sump
Under Footing
| Sump | 2 | 2.65 | 2.65 | 0.1 | 1.4045 | Cum
[5 empty] | Total | 2 | Cum
| TOTAL ATT Qty. |  |  |  |  | 2 | Cum
5 | R.C.C
Sump For R&D and Collection Sump
a) | Under Raft
| Sump | 2 | 2.5 | 2.5 | 0.175 | 2.1875 | Cum
| Total footings RCC |  |  |  |  | 3 | Cum
b) | RCC WALL
Sump For R&D and Collection Sump
Below FFL
| RCC Wall For Sump All round Length | 2 | 8.4 | 0.175 | 1.5 | 4.41 | Cum
| Total columns RCC (upto FFL) |  |  |  |  | 5 | Cum
| Columns |  | RCC Wall Below FFL |  |  | 5 | Cum
e) | Roof Slab
Sump For R&D and Collection Sump
Sump Top Slab
| Slab-1 | 2 | 2.1 | 2.1 | 0.15 | 1.323 | Cum
[6 empty] | 2 | Cum
| Sump Roof Slab |  | Ground Floor |  | TOTAL | 2 | Cum
RCC Concrete Work
| Total Rcc Qty. All Works Upto Plinth Level. |  |  |  |  | 10 | Cum
| Total Rcc Qty. All Works Above Plinth upto Floor V Level |  |  |  |  | 0 | Cum
|  |  |  | Grand Total |  | 10 | Cum
6 | Supplying & Fabrication of Reinforcement steel
Sump For R&D and Collection Sump
| Footings- 60 kg/cum |  | 3 | X | 60 | 180 | kg
| Plinth Beam- 150 kg/cum |  | 0 | X | 150 | 0 | kg
| Columns-250 kgs/cum |  | 0 | X | 250 | 0 | kg
| Roof beams-250 kgs/cum |  | 0 | X | 250 | 0 | kg
| Slabs-80 kgs/cum |  | 2 | X | 80 | 160 | kg
| Stair case-100 kgs/cum |  | 0 | X | 100 | 0 | kg
| RCC Wall -200kgs/cum |  | 5 | X | 200 | 1000 | kg
| Lintels etc., -80 kg/cum |  | 0 | X | 80 | 0 | kg
| Chajjas etc., -60 kg/cum |  | 0 | X | 60 | 0 | kg
|  |  | 10 |  |  | 1340 | kg
| Add : 5% Extra for Other Unforessen Items |  |  |  |  | 67 | kg
[6 empty] | 1407 | KG
[5 empty] | (or) | 2 | MT
7 | SHUTTERING
Sump For R&D and Collection Sump
Under Raft
| Sump | 2 | 10 |  | 0.175 | 3.5 | Sqm
| Total Foundation Shuttering |  |  |  |  | 4 | Sqm
RCC WALL
Below FFL
| RCC Wall For Sump All round Length | 2 | 17.15 |  | 1.5 | 51.45 | Sqm
[6 empty] | 57 | Sqm
| Rcc Wall Below FFL Shuttering |  | RCC (upto FFL) |  |  | 57 | Sqm
Shuttering For Roof Slab
Sump Top Slab
| Slab-1 | 2 | 2.1 | 2.1 |  | 8.82 | Sqm
[6 empty] | 10 | Sqm
| Shuttering for Slabs |  |  |  |  | 10 | Sqm
8 | Water Proofing Treatment
Sump For R&D and Collection Sump
| Under Sump | 2 | 2.3 | 2.3 |  | 10.58 | Sqm
| Walls | 2 | 8.4 |  | 1.5 | 25.2 | Sqm
[6 empty] | 39 | Sqm
| Total Water Proofing Treatment QTY. |  |  |  |  | 39 | Sqm
SEWAGE
9 | Inspection Chamber
| IC 450 x 600 mm | 1 | 10 |  |  | 10
| Total Qty |  |  |  |  | 10 | Nos
10 | Manhole
| 500mm Dia Top and 1200mm Dia Bottom | 1 | 32.5745 |  |  | 32.5745
| Total Qty |  |  |  |  | 36 | Nos
11 | Sump cover with frame of size 600x600mm
| 600X600mm Size | 1 | 4 |  |  | 4
| Total Qty |  |  |  |  | 4 | Nos
12 | 150mmØ SWR /PVC SOIL WASTE PIPE | 1 | 651.49 |  |  | 651.49 | Rmt
[6 empty] | 651 | Rmt
WATER SUPPLY
13 | 25mmØ CPVC Line | 0 | 187 |  |  | 0 | Rmt
[6 empty] | 0 | Rmt
14 | 40mmØ CPVC Line | 0 | 197 |  |  | 0 | Rmt
[6 empty] | 0 | Rmt
15 | Gate Valve
| 25mm dia | 1 | 5 |  |  | 5
| 32mm dia | 1 | 3 |  |  | 3
[6 empty] | 8 | Nos
16 | Septic Tank
| Frame Size 600x600 mm Size | 0 | 2 |  |  | 0
[6 empty] | 0 | Nos
17 | Encapsuled PVC Steps
| Pvc Steps | 1 | 40 |  |  | 40
[6 empty] | 40 | Nos